ROCKWELL AUTOMATION	PROCUREMENT SPECIFICATION

PROCUREMENT SPECIFICATION

Power Quality Monitor

PowerMonitor 5000( M6

NOTICE: The specification guidelines in this document are intended to aid in the specification of products. Specific installations have specific requirements, and Rockwell Automation does not recommend or intend any specific application based solely upon the guidelines provided here. Because of the variety of uses for this information, the user of, and those responsible for applying this information, are responsible for ensuring the acceptability of each application and appropriate use of the guidelines. In no event will Rockwell Automation be liable for misuse, misapplication or reliance on these guidelines in connection with any specific application. Rockwell Automation also disclaims indirect or consequential damages resulting from the use or application of this information.

Note: To download or view a .doc file version of this procurement specification, please visit: www.rockwellautomation.com/industries/procurement-specifications

TABLE OF CONTENTS

PART 1 GENERAL	3

1.01	SUMMARY	3

1.02	RELATED DOCUMENTS	3

1.03	REFERENCES	3

1.04	PRE-MANUFACTURE SUBMITTALS	4

1.05	FINAL SUBMITTALS	4

1.06	QUALITY ASSURANCE	5

1.07	DELIVERY, STORAGE AND HANDLING	5

1.08	WARRANTY	5

1.09	MAINTENANCE	5

PART 2 PRODUCTS	6

2.01	MANUFACTURERS	6

2.02	CONSTRUCTION	6

2.03	VOLTAGE AND CURRENT SENSING	7

2.04	STATUS INPUTS	7

2.05	FUNCTIONS	8

2.06	RELAY OUTPUTS	8

2.07	COMMUNICATION	9

2.08	CONFIGURATION	9

2.09	DISPLAY MODULE (OPTIONAL)	10

2.10	GENERAL RATINGS	11

PART 3 EXECUTION	11

3.01	EXAMINATION	11

3.02	INSTALLATION	11

SECTION XX XX XX

POWER QUALITY MONITOR

GENERAL

SUMMARY

The Power Quality Monitor shall meet the criteria of this specification for energy monitoring.

RELATED DOCUMENTS

Drawings and general provisions of the contract apply to this section.

The following sections contain requirements that relate to this section:

Section 26 09 13 – Electrical Power Monitoring and Control

Section 01 33 00 – Submittal Procedures

Section _______________________________

REFERENCES

The power quality meter shall adhere to the following certifications, approvals and standards:

cULus Certified.

Meets UL61010-1, CSA C22.2 No. 61010-1

UL 61010 Listed, File E345550, for Measuring, Testing and Signal-Generation Equipment.

CE Compliant, tested to meet:

Council Directive 2004/108/EC Electromagnetic Compatibility

Council Directive 2006/95/EC Low Voltage

IP10 degree of protection per IEC 60529 / NEMA/UL 61010

IEEE 519

Recommended Practices and Requirements for Harmonic Control in Electrical Power Systems

IEEE 1159

Recommended Practice for Monitoring Electric Power Quality

IEC 61000-4-30

Testing and measurement techniques – Power quality measurement methods

ANSI C12.20 -2010 Class 0.2 Clause 5.5.4

American National Standard for Electricity Meters – accuracy and performance

EN 62053-22 -2003 Class 0.2 Accuracy

Electricity metering equipment (AC) – Static meters for active energy

EN 61010-1:2001

Safety requirements for electrical equipment for measurement, control and laboratory use – Part 1: General requirements

EN 61326-1:2006

Electrical equipment for measurement, control and laboratory use – EMC requirements – Part 1: General requirements

EN 61000-6-4:2007

Electromagnetic compatibility (EMC) – Part 6-4: Generic standards – Emission standard for industrial environments (Class A)

EN 61000-6-2:2005

Electromagnetic compatibility (EMC) – Part 6-2: Generic standards – Immunity for industrial environments

AS/NZS CISPR 11:2002, Group 1, Class A

Limits and Methods of Measurement of electronic disturbance characteristic of industrial, scientific and medical (ISM) radio frequency equipment

The power quality meter’s control relay outputs shall be ANSI/IEEE tested to meet or exceed C37.90 Trip Duty: 2005 for protective relays and relay systems on all power-connection circuit terminations.

The optional display module shall be designed to meet the following agency approvals.

c-UL-us listed, Hazardous Locations Class I, Division II, Groups A,B,C,D certified

CE marked for all applicable directives

C-Tick marked for use in continental Australia

KCC marked for use in Korea

PRE-MANUFACTURE SUBMITTALS

Refer to Section _________ for submittal procedures.

Product Data

Publications on power quality monitor.

Data sheets on all furnished options.

Installation Instructions

A copy of the manufacturer’s installation instructions, including receiving, handling and storage instructions.

FINAL SUBMITTALS

Refer to Section ________ for procedure on submittal of final documentation.

Supplier Certification

The supplier shall provide certification that the power quality monitor settings have been properly adjusted.

Maintenance Data

Power quality monitor installation instructions and User Manual.

Parameter listing.

QUALITY ASSURANCE

The supplier shall provide power quality monitor system components by a single manufacturer:

Only communication modules for communication or network media functions that are not provided by the power quality monitor manufacturer may be produced by third-party sources.

Only power quality meter manufacturer-approved hardware, including cables, mounting hardware, connectors, enclosures, racks, communication cables, splitters, terminators, taps and removable media, may be used.

All power quality monitor system components shall be new, free from defects and produced by manufacturers regularly engaged in the manufacture of these products.

DELIVERY, STORAGE AND HANDLING

The supplier shall deliver power quality monitor components in packaging designed to prevent damage from static electricity and physical damage.

The supplier shall store the equipment according to manufacturer requirements and in a clean and dry space at an ambient temperature range of:

Power quality meter: -40 to 85°C (-40° to 185°F).

Display module (optional): -25 to 70 ºC (-13 to 158 ºF).

The supplier shall protect the components from exposure to dirt, water, fumes, corrosive substances and physical damage.

WARRANTY

The manufacturer shall provide their standard parts warranty for eighteen (18) months from the date of shipment or twelve (12) months from the date of being energized, whichever occurs first.

This warranty applies to power quality monitors.

MAINTENANCE

As specified in Section __________.

Provisions shall meet the following installed-spare requirements:

Power quality meter:

One spare set of fuses for each type used for the installation.

One spare shorting block for each type used for the installation.

Display module (optional):

Antiglare overlay kit.

Real-time clock replacement battery.

PRODUCTS

MANUFACTURERS

Allen-Bradley – PowerMonitor 5000( M6 Power Quality Monitor (No substitutions)

CONSTRUCTION

    - The power quality monitor shall consist of:

Power quality meter

Display module (optional)

The power quality meter shall:

Connect to a three-phase or single-phase AC power system.

Convert instantaneous voltage and current values to digital values and use the digital values to calculate parameters.

Maintain internal datalogs and record metering, status, event and alarm data into these logs as specified in the logging configuration.

Communicate developed data to controllers, HMI software, applications or its display module (optional).

The power quality meter shall be mounted in a suitable enclosure.

The enclosure shall protect:

The power quality meter from atmospheric contaminants.

The user against personal contact with energized circuits.

When installed within a substation or switchgear lineup, the power quality meter shall be mounted within a low-voltage cubicle, isolated from medium and high-voltage circuits.

The power quality meter shall be designed to operate in:

An industrial environment with an ambient temperature of -20° to 70°C (-4° to 158°F), and with a relative humidity range of 5% to 95%, non-condensing.

A free airflow environment (convection cooling only, no fans or other air moving devices shall be required).

The power quality meter shall be mounted to a well-grounded surface to limit the effects of noise due to electromagnetic interference (EMI).

The power quality meter shall operate with control power electrical service of:

(L1, L2) 120/240 VAC, 50/60 Hz (38 VA) [or 120/240 VDC (26 VA)] nominal

24 VDC (12 VA) nominal

The power quality meter shall include adequate memory to store all necessary data.

Readily accessible on the power quality meter shall be several ports, status indicators and terminal connections, including:

Standard RJ45 Ethernet jack with LNK and ACT indicators.

Optional communications port.

USB Mini-B device port for connection to a host device.

Device and network status indicators.

Power status indicator.

Status input, KYZ output and control relay wiring terminals.

Voltage sensing wiring terminals and current sensing wiring openings.

Virtual wiring connection indicator.

The power quality meter shall have a configuration lock switch.

The optional display module shall be mounted separately and shall be capable of displaying data for up to 3 power quality meters.

VOLTAGE AND CURRENT SENSING

The power quality meter shall monitor 4 voltage and 4 current channels for each electrical cycle.

Provides 1024 samples across 8 channels every cycle.

Measures up to the 127th harmonic.

The voltage sensing connections, current sensing wiring and metering mode shall be selected to match the configuration of the monitored circuit, including:

3-phase, 4-wire Wye

3-phase, 3-wire grounded Wye

3-phase, 4-wire impedance grounded Wye

3-phase, 3-wire Delta or ungrounded Wye

Split-phase/Single-phase

3-phase, 3-wire Delta, grounded B phase (up to 690V L-L)

3-phase, 4-wire high-leg (wildcat)

For voltage sensing, the power quality meter shall be connected:

Directly, for circuits up to 690V L-L.

With potential transformers (voltage transformers), for circuits above 690V L-L.

Voltage sense inputs (V1, V2, V3, VN) shall be rated:

Accuracy in percent of reading at 25°C: ±0.1%.

Input impedance: 5 MΩ minimum.

Input current: 1 mA maximum.

Current sense inputs (I1, I2, I3, I4) shall be rated:

Accuracy in percent of reading at 25°C: ±0.1%.

Overload withstand: 22 A continuous, 200 A for 1 sec.

Burden and Impedance: Negligible.

Maximum crest factor at 5 A: 4.0.

Starting current: 5 mA.

STATUS INPUTS

The power quality meter’s status inputs shall be able to connect to up to 4 non-powered contacts for data collection. The status inputs are contact closure (internal 24 VDC).

FUNCTIONS

Measured parameters shall include:

| Voltage, L-L and L-N | Apparent energy, kVAh |
| --- | --- |
| Current, per phase and total | Real power demand, kW |
| Frequency, last cycle and average | Reactive power demand, kVAR |
| Voltage imbalance | Apparent power demand, kVA |
| Current imbalance | Projected kW demand |
| Real power, kW | Projected kVAR demand |
| Symmetrical Component Analysis | Projected kVA demand |
| Reactive power, kVAR | Demand power factor |
| Apparent power, kVA | Crest factor, V and I – phase |
| True power factor – phase, total | IEEE THD %, V and I – phase, avg |
| Displacement PF – phase, total | IEC THD %, V and I – phase, avg |
| Reactive energy, kVARh | Harmonic content, V and I to 63rd |
| Real energy, kWh | K-factor, I – phase |

Logging functions shall include:

| Energy log | Trigger data log |
| --- | --- |
| Data log | Setpoint log |
| Min/max log | Alarm log |
| Load factor log | Power quality log |
| Time of use logs | Sag/swell events |
| Event log | Oscillography |
| Waveform log | Harmonic analysis |
| Snapshot log |  |

Other functions shall include:

| Security | Logical setpoint programming |
| --- | --- |
| Wiring diagnostics | Waveform synchronization broadcast |
| Virtual wiring correction | User-configurable sag/swell detection |
| Network time synchronization | CIP energy object |
| Network demand synchronization | IEEE 519 harmonics pass/fail |
| Setpoint programming | IEEE 519 TDD (Total Demand Distortion) |

RELAY OUTPUTS

3 relay outputs shall be available for applications including: control of loads, switching of circuit breakers and signaling. The outputs are rated:

Maximum resistive load switching:

50/60 Hz AC RMS: 10 A at 240V (2400 VA)

DC: 10 A at 24V; 0.25 A at 125V

Minimum load switching:

50/60 Hz AC RMS: 10 mA at 5V

DC: 10 mA at 5V

UL 508, CSA 22.2, IC rating class:

50/60 Hz AC RMS: B300

DC: Q300

Maximum make values (inductive load):

50/60 Hz AC RMS: 30 A at 120V; 15 A at 240V (3600 VA)

DC: 0.55 A at 125V; 0.27 A at 240V (69 VA)

Maximum break values (inductive load):

50/60 Hz AC RMS: 3 A at 120V; 1.5 A at 240V (360 VA)

DC: 0.55 A at 125V; 0.27 A at 240V (69 VA)

Maximum motor load switching:

50/60 Hz AC RMS: 1/3 HP at 125V; 1/2 HP at 240V

Protective relays/relay systems rating: ANSI C37.90 Trip Duty: 2005

A KYZ solid-state relay output shall be available for connection to an external pulse accumulator or controller. The output is rated 80 mA at 240 VAC / VDC.

COMMUNICATION

The power quality meter shall have at least:

USB Mini-B connection for a host PC to access the unit’s built-in web pages.

Ethernet connection to support:

EtherNet/IP network.

Access to built-in web pages.

The manufacturer shall have available:

DeviceNet network connection option.

ControlNet network connection option.

CONFIGURATION

The power quality meter shall have internal web pages for configuration, real-time data viewing, diagnostics and maintenance.

The power quality meter shall have configurable alarms for up to 20 events (setpoints), including:

Standard setpoints.

Relative setpoints that can be calculated, such as rolling averages over intervals.

Logical setpoints that can use standard and relative setpoints as inputs, then be configured using 10 logic gates (each with up to 4 inputs), supporting AND, NAND, OR, NOR, XOR and XNOR functions.

The power quality meter shall provide 5 configurable threshold values for voltage sags and 4 values for voltage swells and shall, at sag/swell detection, record event time, event duration, configured threshold and minimum sag/maximum swell, providing sufficient information to classify each event per IEEE 1159 and EN 50160.

The power quality meter shall be configurable to alert other monitors in the system whenever a power quality event is triggered.

The power quality meter shall be configurable to record waveforms for current and voltage inputs, automatically when an RMS voltage variation occurs or when a manual capture command is issued.

The power quality meter shall have virtual wiring correction capability to correct miswiring during commissioning.

The power quality meter shall be scalable and capable of full integration into a plant-wide network.

When connected with other equal power quality meters, its system event snapshot tool contributes to a system-wide event picture.

When used with FactoryTalk( EnergyMetrix software, the power quality meter provides data for power quality analytics.

DISPLAY MODULE (OPTIONAL)

The display module shall have a flat panel display to provide visualization for data from up to 3 power control meters, using built-in software.

The display area shall be 95 mm wide by 53.9 mm high (3.74 inches wide by 2.12 inches high).

      - The display shall be 4-inch color transmissive TFT.

      - The operator input shall be touch screen and 4 function keys.

      - Communication shall be both:

RS-232 (DF1), RS-232 (DH-485), RS-485.

Ethernet.

      - The back of the display module shall have a diagnostic status indicator.

      - The display module shall have a real-time clock with battery backup. The battery is replaceable.

The display module shall be designed to operate in a temperature range of 0 to 50 ºC (32 to 122 ºF) and a humidity range of 5 to 95% non-condensing.

The display module shall operate on power input of 18 to 30 VDC (24 VDC nominal). A DIN-rail-mounted, AC-to-DC power supply 85 to 265 VAC, 47 to 63 Hz option shall be available.

The operator interface terminal shall have one Universal Serial Bus (USB) type-A connector port to connect to removable USB flash drives for external storage.

The operator interface terminal shall have one Universal Serial Bus (USB) type-B connector port (device port) to connect to a host computer using TCP/IP communication and the USB function RNDIS client.

The display module shall be capable of being configured by using the PanelView Explorer Startup window on a browser, using either its USB port or an Ethernet network connection.

Navigation on the display module’s application shall begin on the Main screen, from which 5 other screens can be selected:

Overview – shows snapshot of the average voltage, average current, total power and average true power factor for up to 3 connected power quality meters.

V.I.F. – shows voltage, current, frequency data.

Power – shows power data for each line.

Power Quality – shows sequence data, K-factors and IEEE/IEC averages.

Energy Demand – shows energy, demand and projected demand.

GENERAL RATINGS

The power quality meter shall be able to withstand:

| Vibration | 2 g |
| --- | --- |
| Shock, Operating Shock, Non-operating | 30 g 50 g |
| Dielectric Withstand | As outlined in UL61010, EN61010 |
| Installation Location | Indoor use |
| Altitude | 2000 m (6560 ft) |

The display module (optional) shall be able to withstand conducted susceptibility tests as outlined in:

| Vibration | IEC 60068-2-6 |
| --- | --- |
| Shock | IEC 60068-2-27 |
| Radiated Emissions | CISPR 11: Group 1, Class A |
| ESD Immunity | EN 61000-4-2 |
| Radiated RF Immunity | EN 61000-4-3 |
| EFT/B Immunity | EN 61000-4-4 |
| Surge Immunity | EN 61000-4-5 |
| Conducted RF Immunity | EN 61000-4-6 |

EXECUTION

EXAMINATION

The supplier shall verify that jobsite is ready to receive equipment.

The supplier shall verify that the jobsite environment can be maintained during and after installation within the service conditions required by the manufacturer of the power quality monitor.

INSTALLATION

Installation shall be in compliance with all manufacturer requirements, instructions and contract drawings, including:

Space surrounding the power quality meter to maintain adequate cooling.

Conditioning of space surrounding the power quality meter enclosure to maintain the manufacturer’s ambient temperature and humidity ranges.

Accessibility of power quality meter diagnostic lights and communication ports – these components shall be free from obstructions at all times.

Interface

The supplier shall provide all required cables and connectors to interface with other equipment.

The supplier shall coordinate size and configuration of enclosure to meet project requirements.

The supplier shall ensure that communication connections and wiring are properly protected in accordance with manufacturer recommendations.

END OF SECTION