ROCKWELL AUTOMATION	PROCUREMENT SPECIFICATION

PROCUREMENT SPECIFICATION

SMC™-50 Reduced Voltage Solid-State Smart Motor Controllers

NOTICE: The specification guidelines in this document are intended to aid in the specification of products. Specific installations have specific requirements, and Rockwell Automation does not recommend or intend any specific application based solely upon the guidelines provided here. Because of the variety of uses for this information, the user of, and those responsible for applying this information, are responsible for ensuring the acceptability of each application and appropriate use of the guidelines. In no event will Rockwell Automation be liable for misuse, misapplication or reliance on these guidelines in connection with any specific application. Rockwell Automation also disclaims indirect or consequential damages resulting from the use or application of this information.

Note: To download or view a .doc file version of this procurement specification, please visit: www.rockwellautomation.com/industries/procurement-specifications

TABLE OF CONTENTS

PART 1 GENERAL	4

1.01	QUALIFICATIONS	4

1.02	REFERENCES	4

1.03	ENVIRONMENTAL REQUIREMENTS	5

1.04	PRE-MANUFACTURE SUBMITTALS	5

1.05	FINAL SUBMITTALS	6

1.06	DELIVERY, STORAGE, AND HANDLING	6

1.07	FIELD MEASUREMENTS	6

1.08	SPARE MATERIALS	6

1.09	WARRANTY	7

PART 2 PRODUCTS	7

2.01	RATINGS	7

2.02	SOLID STATE REDUCED VOLTAGE CONTROLLER UNIT DESIGN	7

2.03	SOLID STATE REDUCED VOLTAGE CONTROLLER UNIT MODES	9

2.04	SOLID STATE REDUCED VOLTAGE CONTROLLER UNIT FEATURES	12

2.05	HIM OPTION	16

PART 3 EXECUTION	16

3.01	MANUFACTURER’S SERVICES	16

3.02	TRAINING	17

GENERAL

QUALIFICATIONS

Manufacturer

The manufacturer shall have a minimum of 25 years of experience in the manufacture of solid-state reduced-voltage controllers.

The approved manufacturers are:

Rockwell Automation Allen-Bradley

Substitutions: None permitted

Support

The manufacturer shall maintain factory trained and authorized service facilities within 100 miles of the project and shall have a demonstrated record of service for at least the previous ten years.

Support personnel are to be direct employees of the manufacturer and be available 24 hours per day through a toll-free number.

The manufacturer shall provide all required start-up and training services.

The approved manufacturers are:

Rockwell Automation Customer Support & Maintenance

Substitutions: None permitted

Certification

To ensure all quality and corrective action procedures are documented and implemented all manufacturing locations shall be certified to the ISO-9001 Series of Quality Standards.

Third party manufacturers and brand labeling shall not be allowed.

Definitions

The Solid-State Reduced-Voltage Controller Unit shall refer to the actual controller unit that will be mounted within the specified enclosure.

The Solid-State Reduced-Voltage Controller System shall refer to the controller unit and all items specified under Controller System Options.

REFERENCES

The controller shall be designed to meet or exceed the applicable requirements of the following agencies.

EN

UL

IEC

CSA

NEMA

IEEE

CCC

The following standards shall be met.

Creep distances and clearances 600V (UL/CSA) and 690V (IEC)

Power terminal markings per EN 50005 and EN 60947-4-2

Dielectric withstand per UL 508 and IEC 947

EMC Emission levels, Conducted Radio & Radiated: Class A per IEC60947-4-2

EMC Immunity levels: per EN/IEC60947-4-2

Surge withstand per IEEEC62.41 and IEC61000-4-5

ENVIRONMENTAL REQUIREMENTS

Confirm to specified service conditions during and after installation of products.

Maintain area free of dirt and dust during and after installation of products.

PRE-MANUFACTURE SUBMITTALS

Refer to Section __________ for submittal procedures.

Manufacturer  Dimension Drawings

Product Data

Publications on solid-state reduced-voltage controller.

Data sheets and publications on all major components including but not limited to the following

Contactors

Circuit breakers and fuse information including time current characteristics

Control power transformers

Pilot devices

Relays

Specification Response

Detailed response to this specification showing where in the literature each requirement is satisfied.

All clarifications and exceptions must be clearly identified.

Installation Instructions

Provide a copy of the manufacturer’s installation instructions which includes the following:

Receiving, handling, and storage instructions

Testing and Test Reports

Testing shall be per manufacturer’s standard.

A copy of the test reports, if available, shall be provided as part of the final documentation.

FINAL SUBMITTALS

Refer to Section ____________ for procedure on submittal of final documentation.

The contractor shall provide certification that the solid-state reduced-voltage controller has been installed in accordance with the manufacturer’s instructions.

The contractor shall provide certification that the Contractor has properly adjusted any timing devices required in the starting circuitry.

Final Drawings

The manufacturer shall provide final drawings reflecting the “As-Shipped” state of the installed equipment.

Manufacturer drawings shall be provided in DWG format.

Manufacturer drawings do not need to be stamped if a drawing schedule is provided that lists the drawing numbers, revision levels, and status of drawings (Preliminary, Approval, Final, etc.)

The contractor shall be responsible for making any changes to the “As-Shipped” drawings from the manufacturer to reflect any field modifications.

Test reports, if available, indicating manufacturer’s standard testing was performed.

Maintenance Data

Solid-state reduced-voltage controller installation instructions and User Manual.

Installation / Operation instructions for major components such as circuit

Parameter listing

Field service report from start-up service

Solid state reduced voltage controller spare parts listing and pricing

Include name and phone number for a local distributor for the spare parts.

DELIVERY, STORAGE, AND HANDLING

The contractor shall coordinate the shipping of equipment with the manufacturer.

The contractor shall store the equipment in a clean and dry space.

The contractor shall protect the units from dirt, water, construction debris and traffic.

During storage the contractor shall connect internal space heaters (if specified) with temporary power.

FIELD MEASUREMENTS

The contractor shall verify all field measurements prior to the fabrication of the solid state reduced voltage controller.

SPARE MATERIALS

Provide one (1) set of three (3) of each size power fuse utilized.

Provide spares equal to 10 percent of the installed quantity for primary and secondary control power fuses.

Provide one (1) spare control relay for each unique relay utilized on the project.

WARRANTY

The manufacturer shall provide their standard parts warranty for eighteen (18) months from the date of shipment or twelve (12) months from the date of being energized, whichever occurs first.

The manufacturer shall confirm this warranty as part of the submittal.

This warranty applies only to stand alone solid-state reduced-voltage controllers.

PRODUCTS

RATINGS

The solid state reduced voltage controller shall accept an input voltage from 200…480V AC or 200…690V AC three-phase plus 10 percent or minus 15 percent.

The solid state reduced voltage controller shall have a short circuit current rating of 65 kA @ 480V with standard circuit breakers and 100 kA with type CC/J/L fuses (up to 600V).

Environmental Ratings

Storage ambient temperature range: -25…+75°C.

Operating ambient temperature range: -20…+40°C as standard and up to 65°C maximum with derating.

The relative humidity range: 5%…95% non-condensing.

Operating elevation: up to 2000 meters as standard and up to 4000 meters maximum with derating.

The manufacturer shall provide a tool for evaluating thermal capabilities of the solid state reduced voltage controller.

SOLID STATE REDUCED VOLTAGE CONTROLLER UNIT DESIGN

The open-type controller device shall be modular, consisting of a power structure and a logic component.

Power Structure

The power structure shall include built-in electronic 3-phase current monitoring and overload protection.

The family of devices must be available from  1…520 A in a line motor connection

The family of devices must be available from 1…899 A when connected inside the delta

The inside the delta mode must be auto configured by the controller

For devices rated 90…180 A, the power structure shall consist of three power poles with integral heat sinks in a single housing

For devices rated 210…520 A, the power structure shall consist of three power poles with integrated heatsinksand mounted separately for ease of maintenance

The power structure shall be modular in design and easily replaceable

Back-to-back SCR pairs shall be the only power switching semiconductor means acceptable.  Diode-SCR (Silicon Controlled Rectifier) combinations shall not be acceptable.

SCRs shall have the following minimum repetitive peak inverse voltage ratings.

1400V for units rated 200…480V

1800V for units rated 200…690V

SCRs shall have built in temperature monitoring sensors.

Use of an External bypass must be an option

The manufacture must supply guidance on obtaining Type 2 coordination per IEC 60947 4-2

Logic Component / Control Module

The logic component shall be a self-contained control module, compatible with the full range of power structures.

The control module shall provide continuous 32-bit digital microprocessor control and supervision of all controller operation, including pulse firing of all 6 SCRs.

The control module shall consist of the following.

Self-tuning power supply accepting control power input from 100…240V AC, 50/60 Hz.

SCR firing circuitry that incorporates an RC snubber network to prevent false firing.

Input / output circuitry (two 24V DC inputs and 2 relay outputs standard).

Four (4) DPI communication ports

Built in multi-color status LEDs

A  reset push button on solid state reduced voltage controller

The control terminals shall have the following characteristics

The control terminal wiring connector shall be easily removable and located on the front top of the device for easy access.

The terminals shall be UL rated for 500V, 7 mA maximum, and accept wires from #24 AWG…#14 AWG.

The terminals are UL Recognized to accept a maximum of two (2) #16 AWG wires per terminal.

The control module shall mount directly to the power structure.

The control module shall be easily removed from the power structure, without the need to disassemble associated printed circuit board assemblies.

The control module shall have conformal coated printed circuit boards as standard.

The control module shall have a battery backed time of day clock

Optional Logic Components

The controller shall have a dedicated bezel used to house an optional human interface module (HIM) for parameter configuration and monitoring.  The HIM shall have the following capabilities:

Full numeric tactile feedback keypad with integrated navigation.

Multi-language support.

Multi-line LCD display.

Dynamic soft keys that change function based on the display.

The controller shall have 4 option ports used to house user selectable option modules.  These shall include the following:

Parameter configure module used to provide limited control parameter configuration using rotary position and SIP switches.

Digital input / output module: the module shall provide four (4) 120/240V AC inputs and three (3) relay outputs.

Motor PTC, ground fault, and external current transformer module. This module shall provide interface capability to all three (3) of the sensors.

SOLID STATE REDUCED VOLTAGE CONTROLLER UNIT MODES

Initial and Pre-Starting Modes

Start Delay pre-start

Shall be programmable from 0…30 seconds.

Integral motor winding heater pre-start

The selectable start option will begin at the end of this option.

Programmable time from 0…1000 seconds.

Programmable current from 0…100% of full load current

Motor tuning function (initial start)

Either automatically initiated by the controller on the initial start sequence of the motor or manually initiated by user.

Starting Modes

Soft start

Programmable initial torque value of 0…90% of locked rotor torque.

Programmable acceleration ramp time from 0…1000 seconds.

Current limit 50…600% of full load current.

Current limit start

Adjustable from 50…600% of motor full load current.

Adjustable ramp time from 0…1000 seconds.

Linear speed acceleration start

Programmable ramp time from 0…1000 seconds

Programmable initial torque value of 0…90% of locked rotor torque.

Programmable current limit from 50…600% of full load current.

Full voltage start

Provides across the line starting.

Ramp time shall be less than 0.1 seconds.

Selectable kickstart

A selectable kickstart, or boost, shall be provided at the beginning of the voltage ramp.

The kickstart shall provide an adjustable pulse of 0…90% of locked rotor torque.

The kickstart time shall be adjustable from 0…2 seconds.

Kickstart shall be available for soft start, current limit start, torque control start, pump start, and dual ramp start.

Pump start

Pump start and stop parameters are typically configured together.

Initial torque programmable from 0…90% of locked rotor torque.

Backspin timer programmable from 0…999 seconds.

Ramp time programmable from 0…1000 seconds.

Torque control start

Starting torque programmable from 0…300 percent of rated motor torque.

Maximum torque programmable from 0…300 percent of rated motor torque.

Ramp time programmable from 0…1000 seconds.

Dual ramp start

Provides two (2) separate start profiles with separately adjustable ramp times, current limit level, initial torque, starting and max torque, and kickstart time and level.

Ramp times programmable from 0…1000 seconds.

Current limit level programmable from 50…600% full load current.

Initial torque programmable from 0…90% of locked rotor torque.

Starting and maximum torque programmable from 0…300% of locked rotor torque.

Timed start

Forces the starting profile to complete the entire user-configured ramp time before applying full voltage.

Start delay

User configurable start delay of 0…30 seconds from the point when the start command is enabled until the start sequence actually occurs.

Applies to any start mode.

Backspin

Provided in order to avoid starting a motor into a backspin condition.

The user-configured time begins to count down after a stop maneuver is complete

All start inputs are ignored until the backspin timer has timed out.

Stopping Modes

Coast-to-stop

No further parameters needed.

Soft stop

The soft stop option shall provide a voltage ramp-down for an extended motor stopping time.

Soft stop shall be initiated by a dedicated Soft Stop input.  A coast-to-rest stop shall still be possible with a separate stop input.

Stop time programmable from 0…999 seconds.

The load shall stop when the motor voltage drops to a point where the load torque is greater than the motor torque

Linear speed deceleration

Stop time programmable from 0…999 seconds.

Current limit level programmable from 50…600% of full load current.

Pump stop

The pump control option shall be implemented to provide closed loop control of a motor to match the specific torque requirements of centrifugal  pumps for both starting and stopping

This shall aid in eliminating the phenomena commonly referred to as “water hammer.”

Stop time programmable from 0…999 seconds.

Pump pedestal programmable from 0…50%.

See section 2.03 B 6 for more information.

Braking Control Modes

Smart Motor Braking, SMB

Stop time programmable from 0…999 seconds.

Braking current programmable from 0…400% of full load current

Accu-Stop

Provide a brake from full speed to a present slow speed and then a brake or coast to stop.

Requires four (4) settings:

SMB setting

A control input that is set for stop

A second input that is set for start

A third input that is set for slow speed

External Braking Control

Will remove power from the motor and enable an external mechanism to brake the motor during the user configured stop time from 0…999 seconds.

When the stop time is complete, the unit will open the auxiliary output and switch to the stopped state.

Preset slow speed

Provides a slow speed for applications requiring a slow speed.

The preset slow speed option shall provide two jog speeds in the forward direction: high (15% of base speed) and low (7% of base speed).

The preset slow speed option shall provide two jog speeds in the reverse direction:  high (20% of base speed) and low (10% of base speed).  Reverse operation of the motor shall be available in the jog mode without the use of a reversing contactor.

The starting current for the slow speed operation shall be user adjustable from 0…450% of the motor’s full load current rating.

The running current for the slow speed operation shall be user adjustable from 0…450% of the motor’s full load current rating.

Running Modes

SCR Control – Normal Run Operation

The unit shall run at full voltage when the unit is at full speed and no external bypass contactor is provided.

SCR Control – Energy Saver Run Operation

Only applies during light motor load situations when enabled by user

The controller reduces current to the motor and thereby saves energy

External Bypass – Optional Run Operation

An external bypass contactor may be configured to operate the motor while running at full voltage and speed.

The controller shall control the external bypass contactor by using one of the auxiliary  relay outputs configured to Ext. Bypass using the output’s configuration parameter

For units rated 90…180 A operation in external bypass mode will require current feedback through the optional PTC/Ground Fault/External Current Transformer Expansion Module (150-SMC2) and an 825 MCMxx current sensor.

For units rated 210…520 A operation in external bypass mode with current feedback can be accomplished using the internal current sensors and an optional current feedback mounting kit.

Emergency Run

A control terminal or network input can be configured as the Emergency Run command input.

When this input is active all faults are disabled.

SOLID STATE REDUCED VOLTAGE CONTROLLER UNIT FEATURES

Overload Protection

Shall meet applicable standards as a motor thermal protective device.

Shall utilize three-phase current sensing.  The use of two current transformers shall be unacceptable.

Make available selectable trip class settings from 5…30 in increments of 1 as standard.

Electronic thermal memory shall provide enhanced motor protection.

Shall provide alternative overload capabilities based on Over Power conditions

Digital Outputs

A minimum of two (2) auxiliary contacts shall be provided, as standard, for customer use

The contacts shall be rated for 240V AC maximum.

Functional operation of the contacts shall be programmable for: normal, up-to-speed, Ext. bypass, Ext brake, aux control, network 1-4.

The relay contacts shall be programmable for normally open (N.O.) or normally closed (N.C.) operation.

The controller shall be scalable to enable adding up to nine (9) outputs.

DPI Serial Communication Port

Four (4) DPI serial communication ports shall be provided as standard.

Port #4 supports optional communication protocol interface modules that shall be available for connection to DH485, ControlNet, DeviceNet, RS485, Profibus, InterBus, EtherNet/IP, RS485 HVAC, CAN open, and Control Net (Fiber).

Refer to the system specification for the options (if any) required.

Metering – the controller shall provide the following motor and/or power system metering functions indicated through the optional LCD display.

Three-phase current

Current per phase

Current average

Three-phase voltage

Volts per phase, phase to phase

Volts, average phase to phase

Volts, phase to neutral

Volts, average phase to neutral

Torque in percent of maximum

Power in Mega Watts (MW)

Real power per phase

Real power

Real demand

Maximum real demand

Reactive power in Mega VAR (MVAR)

Reactive power per phase

Reactive power

Reactive demand

Maximum reactive demand

Apparent power in Mega VA (MVA)

Apparent power per phase

Apparent power

Apparent demand

Maximum apparent demand

Energy in Mega Watt hours (MWh)

Real energy

Real demand

Reactive energy in Mega VAR hours (MVARh)

Reactive energy C

Reactive energy P

Reactive energy

Apparent energy in Mega VA hours (MVAh)

Power factor

Power factor per phase

Power factor

Energy savings in percent

Elapsed time in hours

Elapsed time, resettable

Elapsed time 2, not resettable

Running time in hours

Motor speed in percent of full speed

Actual start time (last 5 starts) in seconds

Peak start current (last 5 starts) in Amps

Total starts

Total Harmonic Distortion (THD)

THD of voltage per phase in percent

THD of current per phase in percent

Line frequency in Hertz

Current imbalance in percent

Voltage unbalance in percent

Event log of last 100 events including start, stops, faults, alarms, and parameter changes

Protection and Diagnostics

Pre-start line fault advising of shorted SCR or missing load connection with phase indication.

Running line fault advising power loss, shorted SCR, or missing load connection.

Pre-start power loss with phase indication.

Over temperature

Open gate with phase indication.

The following programmable protection shall be provided as standard with the controller.

Overload

Underload

Undervoltage

Overvoltage

Current imbalance

Voltage unbalance

Phase reversal

High and low line frequency

Stall

Jam

Real power

Motor over power real

Motor under power real

Reactive power

Motor over power reactive + motor generated

Motor under power reactive + motor generated

Motor over power reactive – motor generated

Motor under power reactive – motor generated

Apparent power

Motor over power apparent

Motor under power apparent

Power factor

Excessive starts per hour

Preventive maintenance

Preventive maintenance hours

Preventive maintenance starts

Line loss

Silicon-Controller Rectifier (SCR) Specific protection

SCR shorted

SCR overtemperature

Open SCR gate

When fault conditions are detected, the controller shall inhibit starting or shutting down SCR pulse firing.

A Snapshot record maintains historical data that describes certain conditions that existed prior to a protection fault. The following instantaneous values should be available:

Volts Phase A-B

Volts Phase B-C

Volts Phase C-A

Current Phase A

Current Phase B

Current Phase C

Power Factor

MtrTherm Usage

Motor Speed

THD Vave

THD Iave

Product Status

Board Temp

Line Frequency

Peak Vline A-N (for Shorted SCR faults)

Peak Vline B-N (for Shorted SCR faults)

Peak Vline C-N (for Shorted SCR faults)

Peak I A (for Shorted SCR faults)

Peak I B (for Shorted SCR faults)

Peak I C (for Shorted SCR faults)

Fault diagnostics shall be indicated by a multi-color LED as standard, four (4) diagnostic LEDs on the option module, or by descriptive text on the optional LCD display. (The exclusive use of fault codes is unacceptable.)

An auxiliary contact that is user programmable for fault indication shall be provided for customer use.

Meter accuracy for diagnostics shall be accurate to 3% over nominal sensing range for current and 1% over entire range for voltage.

HIM OPTION

LCD Display

An alphanumeric, backlit LCD display shall be provided for controller set-up, diagnostics, status and monitoring.  The display shall be four-line, 16 characters minimum

Digital parameter adjustment shall be provided through a keypad.  Analog potentiometer adjustments are not acceptable.

EXECUTION

MANUFACTURER’S SERVICES

The service division of the manufacturer shall perform all start-up services.

Start-up personnel shall be direct employees of the manufacturer and shall be degreed engineers.

At a minimum, the start-up service shall include:

Pre-power check

Megger motor resistance: phase-to-phase and phase-to-ground

Verify system grounding per manufacturer’s specifications

Verify power and signal grounds

Check connections

Check environment

Power-up and commissioning

Measure incoming power phase-to-phase and phase-to-ground

Measure DC bus voltage

Measure AC current unloaded and loaded

Measure output voltage phase-to-phase and phase-to-ground

Recording of all measurements

Tuning for system operation

Providing a parameter list

TRAINING

Manufacturer to provide a quantity of one (1) session of on-site instruction.

The service engineer shall perform training.

The instruction shall include the operational and maintenance requirements of the controller

The basis of the training shall be the installed controller, the engineered drawings and the user manual.  At a minimum, the training shall do the following:

Review of the engineered drawings identifying the components shown on the drawings.

Review starting / stopping options for the controller.

Review operation of the Human Interface for programming and monitoring of the controller.

Review the maintenance requirements of the controller.

Review safety concerns with operating the controller.

End of section.

Rockwell Automation, Rockwell Software, Allen-Bradley, CENTERLINE 2100, ArcShield, IntelliCENTER software, Powermonitor 3000, SMC-Flex, SMB, Accu-Stop, SMC-3, PowerFlex 40, PowerFlex 70, and PowerFlex 700 are trademarks of Rockwell Automation, Inc.

Trademarks not belonging to Rockwell Automation are property of their respective companies.