## Introduction
ArmorStart 24V DC Auxiliary Power Calculation Reference Data
About This Publication | This publication provides current capacity sizing calculations for 24V DC control power supplies used on ArmorStart® ST and ArmorStart LT controllers. All of the computations in this calculator come from the companion document, ArmorStart 24V DC Control Power Design Application Guide, publication 280-AT004.
For details about the computations performed in this calculator and for more information regarding 24V DC power supply implementation for ArmorStart controllers, see: ArmorStart 24V DC Control Power Design Application Guide, publication 280-AT004
| ArmorStart 24V DC Control Power Design Application Guide, publication | 280-AT004
Important: Rockwell Automation is not responsible for any content or format changes made by other parties after downloading this spreadsheet file. The original file can be re-downloaded at any time.
TIP: When you search for information in a spreadsheet, set the search options to search the workbook, rather than the current sheet (tab).
Your comments help us serve your documentation needs better. If you have any suggestions on how to improve our content, complete the form at: |  |  | rok.auto/docfeedback
Allen-Bradley, ArmorStart, expanding human possibility, and Rockwell Automation are trademarks of Rockwell Automation, Inc. Trademarks not belonging to Rockwell Automation are property of their respective companies.
280-RD001B-EN-P - February 2024
Supersedes Publication 280-RD001A-EN-P - September 2022 |  |  |  | Copyright © 2024 Rockwell Automation Inc. All Rights Reserved. Printed in USA.

## Instructions
Instructions
• If prompted after opening the file, be sure to enable Macros.
• If there is data already entered in the Product Information tab, click on the "Clear All" button.
• Enter the data requested in the Product Information tab in sequential order. Start with question 1 and continue up to question 11, in order.
• If a question does not apply to your application, skip it.
• Make sure to read the questions carefully so that the correct value is entered in each requested field.
• If you discover that data was entered incorrectly in a previous field, the recommendation is to press the "Clear All" button and start over. Some warnings are present that indicate if the data entered in the answer fields is incorrect, for the questions in the Product Information tab. However, these warnings only work when the data is entered sequentially. So changing the data of a previously answered question may cause the warnings not to appear if a current question is answered incorrectly.
• Current capacity is provided for the following scenarios at the bottom of the Product Information tab:
• Switched (terminals A1 and A2) and Unswitched (terminals A3 and A2) - share the same power source
• Switched (terminals A1 and A2) and Unswitched (terminals A3 and A2) - use separate power sources
Important
This calculator is designed to assist you in sizing the 24V DC power supplies for ArmorStart LT and ArmorStart ST controllers. It is up to you to ensure that the data entered is accurate. You are responsible for the results obtained from this calculator and for selecting the correct power supplies for your application.

## Product Information
1 | What's the total number of ArmorStart LT and ArmorStart ST connected to the same power supply? Please fill in the box below
Number of ArmorStart LT:
Number of ArmorStart ST:
2 | How many ArmorStart start or drive start simutalneously? Please fill in the box below
Number of ArmorStart LT:
Number of ArmorStart ST:
3 | How many ArmorStart LT are the VFD Version (294)?
How many ArmorStart ST are the VFD Version (284)?
4 | Knowing ArmorStart LT Source Brake(EM) is an option, how many drives will use EM brake in the application?
Knowing ArmorStart ST comes to equip Source Brake(EM), how many drives will use EM brake in the application?
5 | How many discrete inputs do you use in your application?
6 | How many discrete outputs do you use in your application?
7 | Does ArmorStart have functional safey? If yes, is it hardwired safety or integrated safety?
8 | How many ArmorStart ST drives are safety version? Please fill in the box below
Number of Starter are safety version (281):
Number of Drive are safety version (284):
9 | How many single channel safety inputs do you use in your application?
How many dual channel safety inputs do you use in your application?
10 | How many safety outputs do you use in your application?
11 | This calculation tool has added x% buffer for sizing power supply, how much extra buffer do you like to set for power supply? Please fill the percentage in the box.
| Please fill the percentage in the box. |  | %
If Switched 24VDC Control Power A1 share the same source as Unswitched 24VDC Control Power A3;
| Total Current | 0
If Switched 24VDC Control Power A1 use and Unswitched 24VDC Control Power A3 use separate power supply;
| Switched 24VDC control power A1 | 0
| Unswitched 24VDC control power A3 | 0
Hardwired Safety
Network Safety
No Safety
Clear All

## Sheet1 (hidden)
|  |  |  | A3 use separate SMPS from A1 | Attributes (Unit Amps) | ArmorStart ST (281,284) |  | ArmorStart LT (290,291,294)
| Units | A1 Current | A3 Current | A3 Current |  | A1/A2 | A3/A2 | A1/A2 | A3/A2
# of AS LT Start Simutalneously | 0 | 0 | 0 | 0 | Inrush Current | 1.09 | 0.3 | 0.45 | 0.45
# of AS ST Start Simutalneously | 0 | 0 | 0 | 0 | Steady State Current | 0.23 | 0.3 | 0.125 | 0.15
# of AS LT to hold | 0 | 0 | 0 | 0 | EM brake (VFD 284,294 only) | 0.125 | 0 | 0.125 | 0
# of AS ST to hold | 0 | 0 | 0 | 0 | Discrete Input | 0 | 0.05 | 0 | 0.05
# of Drive with EM brake | 0 | 0 | 0 | 0 | Discrete Output | 0.5 | 0 | 0.5 | 0
# of discrete Inputs | 0 | 0 | 0 | 0 | Safety contactor | 0.125 | 0.002 | 0 | 0
# of discrete Outputs | 0 | 0 | 0 | 0 | Safety Input(281/284 ES/GS only) | 0 | 0.002 | 0 | 0
# of safety contactor | 0 | 0 | 0 | 0 | Safety Output(281/284 ES/GS only) | 1 | 0 | 0 | 0
# of Safety Inputs | 0 | 0 | 0 | 0
# of Safety Outputs | 0 | 0 | 0 | 0
Total | 0 | 0 | 0 | 0
buffer | 0 | 0 | 0 | 0
0.11

## Summary of Changes
Summary of Changes
Date | Changes
February 2024 | Corrected calculation for safety outputs.