## Introduction
Armor PowerFlex AC Drives Event Codes Reference Data
About This Publication | This publication lists the event codes for Armor PowerFlex AC Drives
For more information see: Armor PowerFlex AC Drives User Manual
35-UM001
Important: Rockwell Automation is not responsible for any content or format changes made by other parties after downloading this spreadsheet file. The original file can be re-downloaded at any time.
TIP: When you search for information in a spreadsheet, set the search options to search the workbook, rather than the current sheet (tab).
Your comments help us serve your documentation needs better. If you have any suggestions on how to improve our content, complete the form at: |  | rok.auto/docfeedback
Allen-Bradley, Armor PowerFlex, expanding human possibility, Rockwell Automation, and Studio 5000 are trademarks of Rockwell Automation, Inc. EtherNet/IP is a trademark of ODVA, Inc. Trademarks not belonging to Rockwell Automation are property of their respective companies.

## Event Codes
Armor PowerFlex Event Codes
For more information see:
Armor PowerFlex AC Drives User Manual 35-UM001
For configurable items in the table below, bold text indicates the default configuration value
Event Code | Event Severity | Associated CIP Object | Description | Corrective Action | Fault Stop Action (default settings in bold)
0x00010001 | Event (4) | Identity | Device Powered Up Logged when a device starts power up initialization, including after a reset. | — | —
0x00010003 | Event (4) | Identity | User Initiated Device Reset Logged when a device is reset by the user, such as via the Identity Reset service. | — | —
0x00050001 | Event (4) | Connection | CIP I/O Connection Opened Logged when a CIP I/O connection has been opened. | — | —
0x00050002 | Event (4) | Connection | CIP I/O Connection Closed Logged when a CIP I/O connection has been cleanly closed (forward close received). | — | —
0x00050003 | Event (4) | Connection | CIP I/O Connection Timed Out Logged when a CIP I/O connection has timed out due to inactivity. | — | —
0x00080001 | Major Fault (8) | Discrete Input Point | Discrete Input Sensor Power Overcurrent Logged when the sensor power current being provided by the product for one discrete input or a set of discrete inputs is above the maximum allowed value. | Check load on the sensor power provided by the input connectors. Combined load cannot exceed 300 mA. | Coast
0x00090001 | Major Fault (8) | Discrete Output Point | Discrete Output Overcurrent Detected Logged when an overcurrent condition is detected on an output point and Short/Overload Fault transitions from false to true. This may also be logged for an output short circuit condition in some products. | • Check load on the user outputs. The combined load on all user outputs cannot exceed 2 A. • Provide a minimum user output load of 10 mA. Current detection does not work reliably without any load and this fault may be reported. | Coast
0x00470001 | Event (4) | Device Level Ring (DLR) | Ring Up Logged when the device level ring transitions to the Normal state. | — | —
0x00470002 | Event (4) | Device Level Ring (DLR) | Ring Down Logged when the device level ring transitions to the Faulted state. | — | —
0x008B0001 | Event (4) | Wall Clock Time | Date/Time Set Logged when the wall clock time value is set to a different value. Devices may choose not to log this event if a set only results in a small change to the previous value (i.e. less than 2 seconds). | — | —
0x008B0002 | Event (4) | Wall Clock Time | Date/Time Invalid Logged when the wall clock time value being used is known to be invalid, such as when a device powers up and detects a hardware clock has not retained the date/time. | — | —
0x00A10001 | Event (4) | Non-Volatile Storage | Firmware Update Started Logged when a firmware update process begins with a reception of an Update or Update2 method call. | — | —
0x00A10002 | Event (4) | Non-Volatile Storage | Firmware Update Completed Logged when a firmware update process is successfully completed (all transfers received and programmed). | — | —
0x00A10003 | Event (4) | Non-Volatile Storage | Firmware Update Failed Logged when a firmware update process is fails due to a bad transfer, fail to program, or other fault (Status attribute values 3, 4, 5). | — | —
0x00A10004 | Major Fault (8) | Non-Volatile Storage | Firmware Update Required A firmware update is required for proper operation of the drive. The current firmware may be obsolete, incompatible, or incomplete. This fault will persist and prevent operation until new firmware is provided. | • Use a tool to perform a network firmware update. This fault persists and prevents operation until new firmware is provided. • If a fault persists after a successful network firmware update, replace the device. (May indicate an internal hardware fault.) | Coast
0x00F50001 | Event (4) | TCP/IP Interface | BOOTP Response Logged when a BOOTP server has sent a response to the device. | — | —
0x00F50002 | Event (4) | TCP/IP Interface | DHCP Response Logged when a DHCP server has sent a response to the device. | — | —
0x00F50003 | Event (4) | TCP/IP Interface | DHCP Renew Logged when the device's DHCP client successfully renews its IP address lease with the DHCP server. | — | —
0x00F50004 | Event (4) | TCP/IP Interface | DHCP Rebind Logged when the device's DHCP client successfully rebinds its IP address lease with the DHCP server. | — | —
0x00F50005 | Event (4) | TCP/IP Interface | DHCP Release Logged when the device's DHCP IP address lease expires. | — | —
0x00F50006 | Event (4) | TCP/IP Interface | Invalid Static Configuration Logged when the device's static network configuration is invalid and the device instead uses DHCP as its network configuration method. | — | —
0x00F50007 | Event (4) | TCP/IP Interface | Duplicate Address Logged when the device detects a duplicate IP address error. | — | —
0x00F60001 | Event (4) | Ethernet Link | Link Up Logged on a transition to the link down state, indicating that the Ethernet link is disabled and unable to send and receive data. | — | —
0x00F60002 | Event (4) | Ethernet Link | Link Down Logged on a transition to the link down state, indicating that the Ethernet link is disabled and unable to send and receive data. | — | —
0x04140001 | Minor Alarm (5) | Predictive Maintenance Component | Maintenance Required Logged when the Remaining Life attribute value is below the configured remaining life threshold, indicating component failure is imminent and maintenance is needed soon. Note that this event may be suppressed (not logged) based on settings in the Predictive Maintenance Component Group object. | • Replace the indicated component, and reset the predictive maintenance data • If the component is an integral part of the device, it is recommended the device be replaced | —
0x04140002 | Event (4) | Predictive Maintenance Component | Reset Performed Logged when a reset of the predictive maintenance data associated with a component (via the Reset Predictive Maintenance Data service) has occurred. | — | —
0x04160001 | Event (4) | Event Log | Event Log Cleared Logged after all event log entries are cleared from an event log using the Reset service. | — | —
0x04160002 | Event (4) | Event Log | Event Log Restore Failure Logged at power up if one or more event log entries could not be restored from non-volatile storage. | — | —
0x04170001 | Event (4) | Fault Alarm | All Faults Acknowledged Logged after all fault entries are acknowledged by the Reset service, or when the fault count goes from a non-zero value to zero. | — | —
0x04170004 | Event (4) | Fault Alarm | Alarm Inactive Logged when the alarm count goes from a non-zero value to zero. That is, this is logged when the product exits the alarm state. | — | —
0x04180001 | Critical Fault (9) | Event Type | Software Critical Fault Occurs when the device software encounters an unexpected condition. | This is an unrecoverable fault that indicates a severe failure with the device firmware. • Cycle power • Perform a firmware update to a newer firmware release • If fault persists, replace the device | Coast
0x04180002 | Critical Fault (9) | Event Type | Hardware Diagnostic Failure Occurs when device hardware behaves unexpectedly, or a hardware diagnostic indicates a potential hardware problem. | This is an unrecoverable fault that indicates a severe failure with the device hardware. • Cycle power • Perform a firmware update to a newer firmware release • If fault persists, replace the device | Coast
0x04190001 | Event (4) | User Configuration | Configuration Operation Start Logged when a configuration transaction operation is started with a Start service | — | —
0x04190002 | Event (4) | User Configuration | Configuration Operation Apply Success Logged when a configuration transaction operation apply occurs using an Apply service, and the new configuration data is successfully validated and applied. | — | —
0x04190003 | Event (4) | User Configuration | Configuration Operation Apply Failure Logged when a configuration transaction operation apply occurs using an Apply service, and the configuration apply fails due to a validation error. | — | —
0x04190004 | Major Fault (8) | User Configuration | Configuration Invalid A previously applied configuration could be restored or used, such as when data corruption or validation errors are detected when restoring the configuration on product power up. In this case, the configuration data / attributes associated with the instance are set to default values. The fault persists until a new, valid configuration is applied. | Re-configure the drive. | Coast
0x04190005 | Major Fault (8) | User Configuration | Configuration Storage Device Error A hardware error was detected with the component being used to store the configuration data for the instance. In this case, the configuration data / attributes associated with the instance are set to default values. The fault persists until a new, valid configuration is applied. | • Re-configure the drive. • If the fault persists, replace the drive. | Coast
0x04190007 | Event (4) | User Configuration | Configure Reset To Default Logged when the configuration data attributes associated with the instance are set to default values (out of box state) by user action. This may occur due to an Identity object out of box reset or some other action. This event should not be logged in cases where the reset of the configuration data to default occurred due to an error. | — | —
0x041B0001 | Event (4) | Motor Control Supervisor | Run Commanded Logged when the Run Commanded attribute transitions from 0 to 1 (true) and the Jog Commanded attribute is 0 (false) (when the drive is not in the special jog mode). | — | —
0x041B0002 | Event (4) | Motor Control Supervisor | Jog Commanded Logged when the Run Commanded attribute transitions to 0 to 1 (true) and the Jog Commanded attribute is 1 (true) (when the drive is in the special jog mode) | — | —
0x041B0003 | Event (4) | Motor Control Supervisor | Stop Request Logged when the Run Commanded attribute transitions from 1 to 0. | — | —
0x041B0004 | Event (4) | Motor Control Supervisor | Direction Commanded Is Forward Logged when the Direction Commanded attribute changes to the forward direction. | — | —
0x041B0005 | Event (4) | Motor Control Supervisor | Direction Commanded Is Reverse Logged when the Direction Commanded attribute changes to the reverse direction. | — | —
0x041B0006 | Event (4) | Motor Control Supervisor | Motor Operation Blocked By Run Inhibit Logged when operation of the motor (via a run or jog command) is blocked or prevented from occurring. When this event is logged, the Last Run Inhibits attribute (if present) is updated, and it can be read to determine the reason(s) motor operation is being prevented. | — | —
0x041B0007 | Event (4) | Motor Control Supervisor | Motor Operation Blocked By Stop Logged when operation of the motor (via a run or jog command) is blocked because a motor control source is commanding a stop. Note this event is a special case of the Motor Operation Blocked By Run Inhibit event, and if both are supported, only this one should be logged in the case the run inhibit bitmask indicates there is an active stop command. | — | —
0x041C0001 | Event (4) | Motor Control Source | Source Data Invalid Logged when an operational source changes operational state from OK to Data Invalid. | — | —
0x041C0003 | Major Fault (8) | Motor Control Source | Source Data Invalid, Fault Occurs when Action, Data Invalid is set to Fault and a motor control operational source changes operational state from OK to Data Invalid. | • Check that the controller that is supposed to be controlling the drive is in Run mode, not Program or Fault mode. • This fault may be expected if the controller is intentionally placed in Program mode. | Coast
0x041C0004 | Event (4) | Motor Control Source | Source Faulted Logged when a motor control operational source changes operational state from OK to Faulted. | — | —
0x041C0006 | Major Fault (8) | Motor Control Source | Source Faulted, Fault Occurs when Action, Faulted is set to Fault and a motor control operational source changes operational state from OK to Faulted. | • Check that the controller that is supposed to be controlling the drive is still powered on and correctly configured. • Verify network cabling. | Coast
0x041C0009 | Event (4) | Motor Control Source | Source Active Logged when a motor control operational source becomes active (is the single source allowed to control motor operation). This is only logged when the active control source (Active Source attribute in Supervisor) changes. Additional events are logged to indicate a change of the active source, such as from remote control via a controller I/O connection (AUTO mode) to control via the keypad (HAND mode). | — | —
0x041D0002 | Event (4) | Motor Configuration | Autotune Begin An autotune operation has begun using the Autotune service (Autotune state) | — | —
0x041D0003 | Event (4) | Motor Configuration | Autotune Complete, Success An autotune operation has completed successfully. Tuning data attributes have been updated with the results. | — | —
0x041D0004 | Major Fault (8) | Motor Configuration | Autotune Failure An autotune operation was started but failed to complete. | • If the failure was caused by a user abort action, restart the autotune procedure. • Otherwise, check if the load is disconnected from the motor. • Or check if the motor is properly connected to the drive. | Coast
0x041E0001 | Event (4) | Velocity Control Supervisor | At Commanded Velocity The drive has reached the commanded velocity (At Commanded Velocity attribute transitions from 0 to 1). | — | —
0x041E0002 | Event | Velocity Control Supervisor | At Zero Velocity The drive has entered a zero velocity state (At Zero Velocity attribute transitions from 0 to 1). | — | —
0x041E0003 | Event (4) | Velocity Control Supervisor | Active Velocity Control Source Changed The active velocity control source (Active Source attribute) has changed. | — | —
0x041E0004 | Event (4) | Velocity Control Supervisor | Commanded Velocity Changed The commanded velocity attribute changed value. | — | —
0x04200001 | Event (4) | Acceleration Control Supervisor | Accelerating The drive started accelerating (Accelerating attribute transitions from 0 to 1). | — | —
0x04200002 | Event (4) | Acceleration Control Supervisor | Decelerating The drive started decelerating (Decelerating attribute transitions from 0 to 1). | — | —
0x04200003 | Event (4) | Acceleration Control Supervisor | Active Acceleration Control Source Changed The active acceleration control source changed. | — | —
0x04230002 | Major Fault (8) | Temperature Sensor | Overtemperature, Hard Temperature value exceeded the Temperature Sensor object High Limit, Hard attribute value. | • Verify that ambient temperature has not exceeded the rated temperature for the device. • If ambient temperature requires derating (running at a lower output current), check that the actual output current meets the derating guidelines. • Verify that the output current is not exceeding the specifications listed in this manual. • Turn off power and allow the product to cool, then retry. | Coast
0x04240001 | Major Fault (8) | DC Bus | Undervoltage, Hard The Measured Voltage value fell below the Voltage Low Limit, Hard. | • Check that the disconnect is in the ON position. • Check for a power quality issue, take appropriate corrective actions. • Check that 3-phase power is present. • Reset the drive. | Coast
0x04240002 | Major Fault (8) | DC Bus | Overvoltage, Hard The Measured Voltage value exceeded the Voltage High Limit, Hard. | • Monitor the AC line for high line voltage or transient conditions. • Motor regeneration can also be the cause of bus overvoltage. Extend the Decel Time setting or install dynamic brake option. • Enable DC bus regulation. | Coast
0x04240005 | Major Fault (8) | DC Bus | Ripple Voltage Over Limit, Hard The ripple voltage value exceeded the Voltage High Limit, Hard value. | • Check that 3-phase power is present(all phases) • Check input fuses • Check input impedance balance • Enable DC bus regulation | Coast
0x04250002 | Major Fault (8) | Inverter | Ground Fault The Ground Current exceeded the threshold. | Check the motor and wiring to the drive for a grounded condition. | Coast
0x04250003 | Configurable: Event (4), Major Alarm (6), Major Fault (8) | Inverter | Output Phase Loss The Output Current of one or more phases fell below the Output Phase Loss Detection Threshold for longer than the Output Phase Loss Detection Time. | • Verify motor wiring. • Decrease the threshold to make the drive less sensitive to trip. | Configurable Coast (1), Ramp (2), Stop, DC Brake (4), Active Stop Mode (255).
0x04250065 | Major Fault (8) | Inverter | Phase 1 (U/T1) To Ground A connection between phase 1 and ground was detected. | • Check the wiring between the drive and motor. • Check motor for grounded phase. • Replace drive if fault cannot be cleared. | Coast
0x04250078 | Major Fault (8) | Inverter | Phase 1 (U/T1) To Phase 2 (V/T2) Short A short between the phase 1 and phase 2 outputs was detected. | • Check the motor and drive output terminal wiring for a shorted condition. • Replace drive if fault cannot be cleared. | Coast
0x04250082 | Major Fault (8) | Inverter | Phase 1 (U/T1) To Phase 3 (W/T3) Short A short between the phase 1 and phase 3 outputs was detected. | • Check the motor and drive output terminal wiring for a shorted condition. • Replace drive if fault cannot be cleared. | Coast
0x042500C9 | Major Fault (8) | Inverter | Phase 2 (V/T2) To Ground A connection between phase 2 and ground was detected. | • Check the wiring between the drive and motor. • Check motor for grounded phase. • Replace drive if fault cannot be cleared. | Coast
0x042500E6 | Major Fault (8) | Inverter | Phase 2 (V/T2) To Phase 3 (W/T3) Short A short between the phase 2 and phase 3 outputs was detected. | • Check the motor and drive output terminal wiring for a shorted condition. • Replace drive if fault cannot be cleared. | Coast
0x0425012D | Major Fault (8) | Inverter | Phase 3 (W/T3) To Ground A connection between phase 3 and ground was detected. | • Check the wiring between the drive and motor. • Check motor for grounded phase. • Replace drive if fault cannot be cleared. | Coast
0x04260001 | Major Fault (8) | Power Supply | Undervoltage, Hard The Measured Voltage value fell below the Voltage Low Limit, Hard. | • Check that the local disconnect is in the ON position. • Check for a power quality issue, take appropriate corrective actions. • Check that 3-phase power is present. • Reset the drive. | Coast
0x04260002 | Major Fault (8) | Power Supply | Overvoltage, Hard The Measured Voltage value exceeded the Voltage High Limit, Hard. | • Monitor the AC line for high line voltage or transient conditions. • Motor regeneration can also be the cause of bus overvoltage. Extend the Decel Time setting or install dynamic brake option. | Coast
0x04260007 | Major Alarm (6) | Power Supply | Power Lost / Not Present The power supply state changed from active to inactive. For an external power supply, this indicates that there is no power input to the product. | This alarm is expected if a power source is intentionally removed from the device. The alarm will go away when the power source is applied again. Consider the following corrective actions if the alarm is not expected: • Check that the local disconnect is in the ON position. • Check for a power quality issue, take appropriate corrective actions. • Check that 3-phase power is present. • Check input fuses. • Check 24V DC power supply | —
0x04260008 | Major Alarm (6) | Power Supply | Power Switched Off, Physical Switch A switchable power supply was switched off by using a physical switch. | • This alarm is expected if the disconnect switch is in the off state. • Place the disconnect switch in the on state(alarm will clear automatically). | —
0x04270001 | Event (4) | Physical Brake Control Supervisor | Brake Release Commanded A command was issued to release the brake. | — | —
0x04270002 | Event (4) | Physical Brake Control Supervisor | Brake Engage Commanded A command was issued to engage the brake. | — | —
0x04270003 | Major Fault (8) | Physical Brake Control Supervisor | Brake State Discrepancy A discrepancy exists between the commanded state and the actual state of the brake. | • Cycle power. • Check EM brake wiring. • If the fault persists, replace the device. | Coast
0x04270004 | Major Fault (8) | Physical Brake Control Supervisor | Brake Fuse Open The brake fuse or circuit breaker is open and control of the brake cannot be performed. | • Check / replace EM brake fuses. • Check input AC fuses. • Check that 3-phase power is present(all phases). | Coast
0x04270005 | Major Fault (8) | Physical Brake Control Supervisor | Brake Overcurrent, Hard The current being used to drive a physical brake exceeded the hardware defined fixed limit for the product. Current to the physical brake is automatically cut off if this fault occurs. | • Check EM brake wiring. • Verify EM brake operation(coil short). • Use EM brake with current draw below device limits. | Coast
0x04270006 | Major Fault (8) | Physical Brake Control Supervisor | Brake Control Hardware Diagnostic Failure The current being used to drive a physical brake exceeded the hardware defined fixed limit for the product. Current to the physical brake is automatically cut off if this fault occurs. | • Cycle power. • If fault persists, replace the device. | Coast
0x04270007 | Configurable: Ignore (0), Event (4), Major Alarm (6), Major Fault (8) | Physical Brake Control Supervisor | Brake Undercurrent, Hard Logged when the current being used to drive a physical brake exceeds the hardware defined fixed limit for the product. Power to the physical brake is automatically cut off if this fault occurs. | • Verify EM brake wiring. • Verify EM brake operation (coil open). • Disable fault if using a EM brake with a low current draw (less than 70 mA). | Configurable Coast (1), Ramp (2), Stop, DC Brake (4), Active Stop Mode (255).
0x04280001 | Event (4) | Physical Brake Control Source | Source Data Invalid Logged when an operational source changes operational state from OK to Data Invalid. | — | —
0x04280003 | Major Fault (8) | Physical Brake Control Source | Source Data Invalid, Fault Occurs when Action, Data Invalid is set to Fault and a physical brake control operational source changes operational state from OK to Data Invalid. | • Check that the controller that is supposed to be controlling the drive is in run mode, not program or fault mode. This fault may be expected if the controller is intentionally placed in program mode. | Coast
0x04280004 | Event (4) | Physical Brake Control Source | Source Faulted Logged when an operational source changes operational state from OK to Faulted. | — | —
0x04280006 | Major Fault (8) | Physical Brake Control Source | Source Faulted, Fault Occurs when Action, Faulted is set to Fault and a physical brake control operational source changes operational state from OK to Faulted. | • Check that the controller that is supposed to be controlling the drive is still powered on and correctly configured. • Verify network cabling | Coast
0x04290001 | Event (4) | Stop Control Supervisor | Stop In Progress A stop command has been accepted and the device begins the stop action (Stopping attribute transitions from 0 to 1). | — | —
0x04290002 | Event (4) | Stop Control Supervisor | Stop Complete The drive completed the stop action and exited the stopping mode (Stopping attribute transitions from 1 to 0). | — | —
0x042B0001 | Major Fault (8) | Dynamic Brake | Resistor Overtemperature The Resistor Overtemperature attribute is true, indicating the dynamic brake resistor is above its maximum allowed temperature. This fault persists until the resistor temperature drops below the maximum temperature. AC power to the resistor is cut. | • Allow dynamic brake resistor to cool If fault appears often: • Verify dynamic brake resistor configuration settings. • Verify duty cycle and time of dynamic brake activation is below maximums specified. • Reduce deceleration times to reduce dynamic braking. • Reduce stop frequency to allow dynamic brake resistor to cool. • Integrated resistor thermal switch may be damaged; Replace dynamic brake resistor. • Check dynamic brake resistor cable /connection. | Coast
0x042B0002 | Major Fault (8) | Dynamic Brake | Resistor Overcurrent The dynamic brake resistor current is above its maximum allowed limit. This fault persists until the dynamic brake resistor current drops below the maximum limit. AC power to the resistor is cut. | • Check dynamic brake resistor cable / connection. • Check that the dynamic brake resistor is approperiate for the drive power rating. (Verify resistor resistance above minimum resistance for the power rating). • Replace dynamic brake resistor. • Replace device. | Coast
0x042F0001 | Major Fault (8) | Feedback | Feedback Signal Loss The Fault attribute transitioned from true to false due to a feedback signal loss fault. | • Verify encoder configuration settings. • Check encoder wiring. | Coast
0x042F0004 | Major Fault (8) | Feedback | Feedback Velocity Comparison Failure The Fault attribute transitioned from true to false due to a feedback velocity comparison fault. | • Verify encoder configuration settings. • Check encoder wiring. | Coast
0x04300003 | Event (4) | Fault Auto Clear Run | Auto Fault Reset And Run Attempt Logged when a fault auto reset and run (restart) attempt is made. | — | —
0x04300004 | Major Fault (8) | Fault Auto Clear Run | Auto Fault Reset And Run Retries Exceeded The number of auto fault reset and run attempts equals the number of configured retries when unacknowledged faults are still present. | Correct the cause of the fault and manually clear. See the user manual for details on how to clear faults. | Coast
0x04320001 | Major Fault (8) | Motor Thermal Overload | Motor Thermal Overload, Hard The Thermal Capacity Utilized attribute is at or above 100%. | • Allow motor to cool and attempt restart. • Check configuration setting for motor overload current. • Reduce load. • Reduce time the motor is in overload, such as by reducing acceleration time and using lower speeds. | Coast
0x04340001 | Configurable: Event (4), Major Alarm (6), Major Fault (8) | Load Monitor | Load Monitor, Above Level (Shear Pin) A load monitor instance tripped (attribute transitions from false to true) due to the power output exceeding the configured level. | • Check for motor stall or machine jam condition. • Reduce the load. • Adjust load monitor current level to be appropriate for the application. | Configurable Coast (1), Ramp (2), Stop, DC Brake (4), Active Stop Mode (255).
0x04340002 | Configurable: Event (4), Major Alarm (6), Major Fault (8) | Load Monitor | Load Monitor, Below Level (Load Loss) A load monitor instance tripped (attribute transitions from false to true) due to the power output being less than the configured level. | • Check if the load has become decoupled from the motor. • Adjust load motor current level to be appropriate for the application. | Configurable Coast (1), Ramp (2), Stop, DC Brake (4), Active Stop Mode (255).
0x04360001 | Major Fault (8) | Inverter Protection | Inverter Overcurrent, Instantaneous The inverter current exceeded the Instanteous Overcurrent Limit. | • Check motor and motor wiring for short circuit. • Reduce load. | Coast
0x04360003 | Major Fault (8) | Inverter Protection | Inverter Overload, Current The inverter is in overload based on the current overload model (Current Capacity Utilized greater than 100%) and no other overload action has been defined. | • Reduce load. • Configure a reduced current limit. • Enable reduced current limit on overload. | Coast
0x04360004 | Major Fault (8) | Inverter Protection | Inverter Overload, Thermal The inverter is in overload based on the thermal overload model (Thermal Capacity Utilized greater than 100%). | • Reduce load. • Configure a reduced current limit. • Enable reduced current limit on overload. • Enable PWM requency reduction on overload. | Coast
0x04380001 | Event (4) | Drive Power Loss Supervisor | Power Loss Condition Present Logged when the active Drive Power Loss Source detects a power loss condition. | — | —
0x043A0001 | Event (4) | Drive Safety Manager | Torque Enabled Logged when the Torque Enabled attribute transitions from false to true, indicating torque is now permitted. | — | —
0x043A0002 | Event (4) | Drive Safety Manager | Torque Disabled Logged when the Torque Enabled attribute transitions from true to false, indicating torque is no longer permitted. | — | —
0x043A0003 | Event (4) | Drive Safety Manager | STO Reaction Logged when the Torque Enabled attribute transitions from true to false, indicating torque is no longer permitted. | — | —
0x043A0004 | Event (4) | Drive Safety Manager | STO Activation Logged when the product detects a STO activation. Products may choose to not log this event and instead only log a "STO Reaction" event if they are immediately reacting to the activation. | — | —
0x043A0005 | Major Fault (8) | Drive Safety Manager | STO Fault An STO fault was detected (STO fault attribute is true). This fault will be reported until the STO fault condition is cleared in the safety logic. | • To clear (reset) the Safety Fault, remove the source of the safety fault and then send a fault reset to the safety logic. • See the user manual for details on Safety Fault Reset. • See the user manual for details on STO Faults. | Coast
0x043A0006 | Event (4) | Drive Safety Manager | Safe Stop 1 Reaction Logged when the product reacts to a safe stop 1 (SS1) activation. | — | —
0x043A0007 | Event (4) | Drive Safety Manager | Safe Stop 1 Activation Logged when the product detects a SS1 activation. | — | —
0x043A0008 | Major Fault (8) | Drive Safety Manager | Safe Stop 1 Fault An SS1 fault was detected. This fault will be reported until the SS1 fault condition is cleared in the safety logic. | • To clear (reset) the Safety Fault, remove the source of the safety fault and then send a fault reset to the safety logic. • See the user manual for details on SS1 Safety Faults. • If using drive based SS1 functionality, check configuration parameters such as deceleration time. | Coast
0x043A000C | Major Fault (8) | Drive Safety Manager | Safety Recoverable Fault Safety logic declared a recoverable fault (Safety Fault attribute is true). Note this fault will be continuously logged while a safety fault is present. | • To acknowledge or clear this fault, remove the source of the safety fault and send a fault reset to the safety logic. • See the user manual for details. | Coast
0x043A000D | Major Fault (8) | Drive Safety Manager | Safety Unrecoverable Fault Safety logic is declared an unrecoverable fault (Safety Unrecoverable Fault attribute is true). This fault is persistent and cannot be cleared without a power cycle. | • Power cycle the device. • If fault persists, replace the device. | Coast
0x043A000E | Major Fault (8) | Drive Safety Manager | Safety Feedback Fault Safety logic reported a problem with a safety feedback device. | • Verify safety encoder configuration settings. • Check encoder wiring. • Safety fault must be cleared via CIP safety connection before the standard fault can be cleared, see user manual. | Coast
0x043A000F | Event (4) | Drive Safety Manager | Safe Brake Released Logged when the safe brake state changes from engaged to released. | — | —
0x043A0010 | Event (4) | Drive Safety Manager | Safe Brake Engaged Logged when the safe brake state changes from engaged to released. | — | —
0x043F0001 | Event (4) | Discrete Output Control Source | Source Data Invalid Logged when a discrete output operational source changes operational state from OK to Data Invalid. | — | —
0x043F0003 | Major Fault (8) | Discrete Output Control Source | Source Data Invalid, Fault Occurs when Action, Data Invalid is set to Fault and a discrete output operational source changes operational state from OK to Data Invalid. | • Check that the controller that is supposed to be controlling the drive is in run mode, not program or fault mode. • This fault may be expected if the controller is intentionally placed in program mode. | Coast
0x043F0004 | Event (4) | Discrete Output Control Source | Source Faulted Logged when a discrete output operational source changes operational state from OK to Faulted. | — | —
0x043F0006 | Major Fault (8) | Discrete Output Control Source | Source Faulted, Fault Occurs when Action, Faulted is set to Fault and a discrete output operational source changes operational state from OK to Faulted. | • Check that the controller that is supposed to be controlling the drive is still powered on and correctly configured. • Verify network cabling. | Coast
0x04400001 | Minor Alarm (5) | Fan | Underspeed, Hard Logged when the Measured Speed value falls below the Speed Low Limit, Hard. | • Check external fan connection to drive. • Verify external fan is not blocked or stuck. • Replace external fan. | —
0x04400002 | Minor Alarm (5) | Fan | Overspeed, Hard Logged when the Measured Speed value goes above the Speed High Limit, Hard. | • Check external fan connection to drive. • Verify external fan is not being rotated by an external force (i.e. by a strong air current blowing on it) • Replace external fan. | —
0x04400005 | Minor Alarm (5) | Fan | State Discrepancy Logged when there is a discrepancy between the commanded state and actual state. The amount of time the states must be discrepant before a discrepancy event is reported is product specific | • Check external fan connection to drive. • Verify external fan is not blocked or stuck. • Replace external fan. | —

## Summary of Changes
Summary of Changes
Date | Changes
April 2022 | First release of this fault code spreadsheet.
August 2023 | Added events for Frame B.