## Introduction
PowerFlex 6000T Drives Conditions Reference Data
About This Publication | This publication lists the conditions for PowerFlex® 6000T Drives
For more information see: PowerFlex 6000T Drives Programming Manual
6000-PM100
Important: Rockwell Automation is not responsible for any content or format changes made by other parties after downloading this spreadsheet file. The original file can be re-downloaded at any time.
TIP: When you search for information in a spreadsheet, set the search options to search the workbook, rather than the current sheet (tab).
Your comments help us serve your documentation needs better. If you have any suggestions on how to improve our content, complete the form at: |  | rok.auto/docfeedback
Allen-Bradley, Connected Components Workbench, ControlLogix, CompactLogix, DeviceLogix, expanding human possibility, FactoryTalk, PowerFlex, Rockwell Automation, Studio 5000 Logix Designer, and TechConnect are trademarks of Rockwell Automation, Inc. EtherNet/IP is a trademark of ODVA, Inc. Trademarks not belonging to Rockwell Automation are property of their respective companies.
Rockwell Automation recognizes that some of the terms that are currently used in our industry, in this publication, and in product help files are not in alignment with the movement toward inclusive language in technology. We are proactively collaborating with industry peers to find alternatives to such terms and making changes to our products and content. Please excuse the use of such terms in our content while we implement these changes.

## Summary of Changes
Summary of Changes
Date | Changes
2023-01-11 | Initial release of this publication

## Port 0
Condition Type | Condition Code | Display Text | Fault | Action | Fault Action | Configuration Parameter | Configurable Action
none | 0 | No Entry
Resettable Fault | 1 | Auxiliary Input | Auxiliary Input The auxiliary fault digital input is open or reset. | Determine where the Auxiliary input function is assigned using parameter 0:115 [DI Aux fault]. Verify that this assigned input is not open or reset. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 4 ‘PERIF Flts’ | 0:115 [DI Aux Fault] | —
Resettable Fault | 2 | Sys Default Fail | System Reset to Defaults Failure A command to reset parameter defaults has failed. The values of some parameters have not been changed. | Verify an I/O connection is not established to the drive. For example, a controller is communicating with the drive. | — Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Alarm 1 | 3 | Emerg OVRD Actv | Emergency Override Activated Emergency override is activated. Faults in the groups that are configured in parameter 0:455 [Emerg Prot OVRD] are ignored if set while emergency override is activated. If faults groups are ignored, the life span of the product can be shortened. Replacement of the product is recommended after the emergency has passed. | Normal operation when Emergency override is activated. Parameter 0:456 [EmergMode Status] displays the status of emergency override mode. To clear, deactivate Emergency override mode. | — | — | —
Event | 7 | EmergOVRD Actv | Emergency Override Activated Emergency override has been activated. | — | — | — | —
Event | 8 | EmergOVRD Deactv | Emergency Override Deactivated Emergency override has been deactivated. | — | — | — | —
Event | 9 | Firmware Started | Firmware Started The application program is starting. | — | — | — | —
Event | 10 | Firmware Stopped | Firmware Stopped Control power was removed. | — | — | — | —
Resettable Fault | 15 | AuRsts Exhausted | Auto Restarts Exhausted The drive unsuccessfully attempted to reset a fault and resume running for the programmed number of tries. | Determine why the Auto Restart function expired. Examine the fault queue for which fault was unable to reset and troubleshoot that fault. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: Cannot override this fault. | 0:61 [Auto Rstrt Tries] | —
Alarm 1 | 16 | CPU OverTemp Alm | CPU Over Temperature Alarm The temperature of the main microprocessor (CPU) on the main control board has exceeded the alarm threshold (103 °C). | Verify adequate airflow and the ambient temperature is within specification. Check whether the control pod fan(s) are functioning properly. | — | — | —
Resettable Fault | 17 | CPU OverTemp Flt | CPU Over Temperature Fault The temperature of the main microprocessor (CPU) on the main control board has exceeded the fault threshold (107 °C). | Verify adequate airflow and the ambient temperature is within specification. Check whether the control pod fan(s) are functioning properly. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 7 ‘Board Faults’ | — | —
Resettable Fault | 18 | System Defaulted | System Defaulted A command to reset parameter defaults has been executed. | — | — Additional Fault Action Fault opens main circuit breaker: N/A Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Event | 21 | Clr Fault Queue | Clear Fault Queue A command to clear the fault queue has been executed. | — | — | — | —
Event | 22 | Clr Alarm Queue | Clear Alarm Queue A command to clear the alarm queue has been executed. | — | — | — | —
Resettable Fault | 23 | Board OT Fault | Control Board Overtemperature Fault The temperature of the main control board has exceeded the fault threshold. • The fault threshold is 90 °C with the control pod fan on. • The fault threshold is 80 °C with the control pod fan off. Possible causes include high ambient temperature and obstructed airflow. The control pod temperature is reported by parameter 0:25 [Ctrl Pod Temp]. | Verify adequate airflow and the ambient temperature is within specification. Check the condition of cabinet air filters. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 7 ‘Board Faults’ | — | —
Alarm 1 | 24 | Board OT Alarm | Control Board Overtemperature Alarm The temperature of the main control board has exceeded the alarm threshold. • The alarm threshold is 85 °C with the control pod fan on. • The fault threshold is 75 °C with the control pod fan off. Possible causes include high ambient temperature and obstructed airflow. The control pod temperature is reported by parameter 0:25 [Ctrl Pod Temp]. | Verify adequate airflow and the ambient temperature is within specification. Check the condition of cabinet air filters. | — | — | —
Resettable Fault | 25 | Board UT Fault | Control Board Undertemperature Fault The temperature of the main control board has fallen below the fault temperature (-25 °C). Possible causes include low ambient temperature and obstructed airflow. | Check the ambient temperature. Check the condition of cabinet air filters. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 7 ‘Board Faults’ | — | —
Alarm 1 | 26 | Board UT Alarm | Control Board Undertemperature Alarm The temperature of the main control board has fallen below the alarm temperature (-15 °C). Possible causes include low ambient temperature and obstructed airflow. | Check the ambient temperature. Check the condition of cabinet air filters. | — | — | —
Resettable Fault | 27 | Module Defaulted | Module Defaulted A command to reset parameter defaults has been executed. | — | — Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 29 | Port 1 Adapter | Port 1 Adapter The DPI communications adapter in port 1 has a fault. Port 1 is the HIM cradle on the control pod. | See device event queue. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 10 ‘Pt1...3 Flts’ | — | —
Resettable Fault | 30 | Port 2 Adapter | Port 2 Adapter The DPI communications adapter in port 2 has a fault. Port 2 is usually a HIM or a 1203-USB adapter. | See device event queue. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 10 ‘Pt1...3 Flts’ | — | —
Resettable Fault | 31 | Port 3 Adapter | Port 3 Adapter The DPI communications adapter in port 3 has a fault. Port 3 is usually a HIM or a 1203-USB adapter. | See device event queue. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 10 ‘Pt1...3 Flts’ | — | —
Resettable Fault | 32 | Port 4 Adapter | Port 4 Adapter The DPI communications adapter in port 4 has a fault. Port 4 is backplane option slot 4. | See device event queue. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 11 ‘Port 4 Flts’ | — | —
Resettable Fault | 33 | Port 5 Adapter | Port 5 Adapter The DPI communications adapter in port 5 has a fault. Port 5 is backplane option slot 5. | See device event queue. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 12 ‘Port 5 Flts’ | — | —
Resettable Fault | 34 | Port 6 Adapter | Port 6 Adapter The DPI communications adapter in port 6 has a fault. Port 6 is backplane option slot 6. | See device event queue. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 13 ‘Port 6 Flts’ | — | —
Configurable | 35 | Port 1 DPI Loss | Port 1 DPI Loss The DPI communications adapter in port 1 has stopped communicating. Port 1 is the HIM cradle on the control pod. | Check connections and grounding. | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 10 ‘Pt1...3 Flts’ | 0:204 [DPI Pt1 Flt Actn] | —
Configurable | 36 | Port 2 DPI Loss | Port 2 DPI Loss The DPI communications adapter in port 2 has stopped communicating. Port 2 is usually a HIM or a 1203-USB adapter. | Check connections and grounding. | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 10 ‘Pt1...3 Flts’ | 0:206 [DPI Pt2 Flt Actn] | —
Configurable | 37 | Port 3 DPI Loss | Port 3 DPI Loss The DPI communications adapter in port 3 has stopped communicating. Port 3 is usually a HIM or a 1203-USB adapter. | Check connections and grounding. | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 10 ‘Pt1...3 Flts’ | 0:208 [DPI Pt3 Flt Actn] | —
Resettable Fault | 38 | Port 4 DPI Loss | Port 4 DPI Loss The DPI communications adapter in port 4 has stopped communicating. Port is backplane option slot 4. | Check connections and grounding. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 11 ‘Port 4 Flts’ | — | —
Resettable Fault | 39 | Port 5 DPI Loss | Port 5 DPI Loss The DPI communications adapter in port 5 has stopped communicating. Port is backplane option slot 5. | Check connections and grounding. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 12 ‘Port 5 Flts’ | — | —
Resettable Fault | 40 | Port 6 DPI Loss | Port 6 DPI Loss The DPI communications adapter in port 6 has stopped communicating. Port is backplane option slot 6. | Check connections and grounding. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 13 ‘Port 6 Flts’ | — | —
Resettable Fault | 43 | PwrDn NVS Blank | Power Down NVS Blank An internal data error occurred. | Reset parameter defaults. Reload parameters. If problem persists, replace main control board. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 13 ‘Port 6 Flts’ | — | —
Non-Resettable Fault | 58 | PwrDn Data Chksm | Power Down Data Checksum Checksum failed for nonvolatile data. | Replace the main control board. Important: Predictive maintenance and run time data on the main control board will be lost. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Connot override this fault. | — | —
Event | 60 | New Firmware | New Firmware New firmware was detected at power up. | — | — | — | —
Event | 61 | Invalid RTC Time | Invalid RTC Chip Time The real time clock (RTC) does not return the value that is written to it. | Cycle power. If fault persists, replace the main control board. | — | — | —
Event | 62 | RTC HW Failed | RTC Hardware Access Failed The real time clock (RTC) hardware and software function are not properly synchronized. | Cycle power. If fault persists, replace the main control board. | — | — | —
Event | 63 | Time Change | Time Change Event The value of the real time clock (RTC) has been adjusted to match an external source. | — | — | — | —
Event | 64 | Pwr Cyc Cnt Ovf | Power Cycle Change Count Overflow The power cycle counter has rolled over (from 65535 to 0). | — | — | — | —
Event | 65 | Time Chg Cnt Ovf | Time Change Count Overflow The time change counter has rolled over (from 65535 to 0). | — | — | — | —
Alarm 1 | 66 | PwrDn Backup | Power Down Backup The back-up power down information has been restored in place of the main power down data due to the main data being erased or corrupted. | — | — | — | —
Resettable Fault | 67 | PwrDn Data Fail | Power Down Data Failure The stored power down data has failed to be retrieved a set amount of times. | Replace the main control board. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Connot override this fault. | — | —
Alarm 1 | 68 | PwrDn Sig Fail | Power Down Signal Failure The power down signal for the main control board has failed. This condition prevents storing of power down data for the application, including energy meters and predictive maintenance data. | Cycle power to the product. If this alarm persists, replace the main control board. | — | — | —
Event | 69 | Cond Data Lost | Condition Data Corrupt Condition data was determined to be corrupt or missing at power up. | — | — | — | —
Event | 70 | Firmware Update | Firmware Update An event to update the firmware image on the product has been triggered. During flashing, the product will not accept I/O connections, and it cannot be started. | — | — | — | —
Alarm 2 | 71 | Bipolar Conflict | Bipolar Conflict Parameter 10:930 [Direction Mode] is set to 1 ‘Bipolar’ or 2 ‘Rev Disable’ and one or more digital inputs is enabled for direction control. | — | — | — | —
Alarm 2 | 73 | DigIn Cfg B | Digital Input Configuration B Digital input conflict. Input functions that cannot exist simultaneously have been selected (for example run and start). See the configuration table on the Tables & Graphics tab. | Correct the digital Input configuration. | — | — | —
Alarm 2 | 74 | DigIn Cfg C | Digital Input Configuration C Digital input conflict. Input functions that cannot be assigned to the same digital input have been selected (for example run and stop). See the configuration table on the Tables & Graphics tab. | Correct the digital Input configuration. | — | — | —
Event | 77 | Drive Reset | Drive Reset A command to reset the product has been received. | — | — | — | —
Event | 80 | Drive Faulted | Drive Faulted A fault has occurred in the product. | — | — | — | —
Event | 82 | Clr Event Queue | Clear Event Queue A command to clear the event queue has been executed. | — | — | — | —
Event | 83 | Clr Excptn Queue | Clear Exception Queue A command to clear the exception queue has been executed. | — | — | — | —
Resettable Fault | 86 | HW Enbl Jmpr Out | Hardware Enable Jumper Out A safety option module is present and the enable is removed. | Install the jumper. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 87 | Safety Brd Fault | Safety Board Fault A Safety option module has indicated a fault. Safe Speed Monitor (20-750-S1): • See nn:67 [Fault Status] on page 398 for more information on the fault statuses. • See publication 750-RM001 for more information. Safe Torque Off (20-750-S): • If DC power drops below 17V DC, ‘Not Enable’ is indicated. • If voltage drops below 11V DC, the module faults. • See publication 750-UM002 for more information. ATEX (20-750-ATEX): • Possible hardware damage. • The motor to the thermal sensor is shorted. • Excessive EMC noise due to improper grounding/shielding. • See publication 750-UM003 for more information. | Verify that enable jumper is installed. Reset or power cycle drive. | Coast (Motor Side Inverter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 88 | Safety Jmpr Out | Safety Jumper Out Safety jumper is not installed and a safety option module is not present. | Install the jumper. | Coast (Motor Side Inverter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 89 | Safety Jumper In | Safety Jumper In Safety jumper is installed and a safety option module is present. | Remove the jumper. | Coast (Motor Side Inverter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 92 | SafetyHealth Err | SafetyHealth Error Safety jumper is installed with incorrect safety circuit status. This fault indicates a hardware anomaly. | Cycle power. If problem persists replace main control board. | Coast (Motor Side Inverter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 93 | SafetyPwrOn Err | SafetyPwrOn Error Safety option card is not detected or ATEX2 is present while safety power is OFF (rather than ON). Indicates a hardware anomaly. | Verify configuration. Cycle power and replace control board and/or any option cards if the drive continues to fault. | Coast (Motor Side Inverter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 94 | SafetyPwrOff Err | Safety Power Off Error Safety option card is detected while safety power is ON (rather than OFF). Indicates a hardware anomaly. | Verify configuration. Cycle power and replace control board and/or any option cards if the drive continues to fault. | Coast (Motor Side Inverter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 95 | FS Enbl Ch Error | FS Enable Channel Error Safety fault is detected and no safety option is present. Indicates a hardware anomaly with drive enable circuitry. | Verify configuration. Cycle power and replace control board and/or any option cards if the drive continues to fault. | Coast (Motor Side Inverter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Alarm 2 | 104 | Port 4 Cfg | Port 4 Configuration The main control board does not have the correct option in the port. | Option may not be compatible with product or MCB firmware needs to be updated to support it. Option may have to be moved or removed, accept option configuration change. | — | — | —
Alarm 2 | 105 | Port 5 Cfg | Port 5 Configuration The main control board does not have the correct option in the port. | Option may not be compatible with product or MCB firmware needs to be updated to support it. Option may have to be moved or removed, accept option configuration change. | — | — | —
Alarm 2 | 106 | Port 6 Cfg | Port 6 Configuration The main control board does not have the correct option in the port. | Option may not be compatible with product or MCB firmware needs to be updated to support it. Option may have to be moved or removed, accept option configuration change. | — | — | —
Alarm 2 | 107 | Port 7 Cfg | Port 7 Configuration The main control board does not have the correct option in the port. | Option may not be compatible with product or MCB firmware needs to be updated to support it. Option may have to be moved or removed, accept option configuration change. | — | — | —
Alarm 2 | 108 | Port 8 Cfg | Port 8 Configuration The main control board does not have the correct option in the port. | Option may not be compatible with product or MCB firmware needs to be updated to support it. Option may have to be moved or removed, accept option configuration change. | — | — | —
Alarm 2 | 112 | Port 12 Cfg | Port 12 Configuration The main control board has detected a configuration change since power down on Port 12. | Acknowledge the new configuration. If a configuration change is not intended, power down and inspect the fiber communication and connections to power peripherals (PCCB). | — | — | —
Alarm 2 | 114 | Port 14 Cfg | Port 14 Configuration The main control board has detected a configuration change since power down on Port 14. | Acknowledge the new configuration. If a configuration change is not intended, power down and inspect the fiber communication and connections to the Peripheral (PIOB). | — | — | —
Event | 129 | Pred Maint Reset | Predictive Maintenance Reset Predictive maintenance function has reset an elapsed life parameter. | — | — | — | —
Configurable | 169 | Rem Med Not Inst | Storage Media Not Installed The drive powered up without removable storage media installed. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Ignore | 0:56 [RemMedEventActn] | —
Resettable Fault | 171 | No Stop Source | All Logic Control Sources Disconnected The last source for a stop command to the motor side inverter has been removed or disconnected. Sources can include a digital input, communication link to a controller, or a HIM. | Connect and configure a source for a stop command. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 4 ‘PERIF Flts’ | — | —
Alarm 2 | 176 | InvldDataSource | Invalid Indirect Selection An indirect selector parameter is configured to point to itself as the data source or is selecting a non-existent parameter or data source. This alarm can occur if a selector is directed to a source that has been removed. Sources can include option cards and modular control profiles, such as the configurable motor control in port 10. For example, parameter 0:108 [DI M Stop] is selecting a digital input on an I/O card in slot 4 and the option card has been removed from slot 4. | Review the parameter configuration. Review the installation and configuration of control sources. | — | — | —
Configurable | 177 | NonStdDataSource | Non Standard Data Source An indirect selector parameter is selecting a parameter or data source that is not included in the selection lists for that parameter. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: N/A | 0:1921 [NonStdDataAct] | —
Alarm 2 | 180 | Invld 2Wire Cfg | Invalid 2 Wire Configuration Run level logic is configured, but no digital input signal is configured for a run logic command. | This alarm can be cleared by changing parameter 0:101 [Digital In Cfg] to run edge or by configuring a digital input signal for parameter 0:120 [DI M Run] or parameter 0:123 [DI L Run]. | — | — | —
Alarm 1 | 182 | NonAuthenticDHCF | Non Authenticated DHCF This condition is raised when the firmware detects that the DHCF in the internal file system could not be authenticated. | — | — | — | —
Alarm 1 | 183 | Invalid DHCF | Invalid DHCF This condition is raised when the firmware detects that the DHCF in the internal file system is Invalid. | — | — | — | —
Fault Major | 184 | Missing DHCF | Missing DHCF This condition is raised when the firmware detects that there is no DHCF in the internal file system. | — | — | — | —
Fault Major | 185 | DHCF Dir Corrupt | DHCF Directory Corrupt This condition is raised when the firmware detects that the internal file system containing the DHCF Directory has been corrupted. | — | — | — | —
Fault Major | 186 | MnlnpDvcOpenRun | Main/Input Device Opened Drv Run This condition indicates that the Main/Input Device opened while the drive is running. | — | Coast Stop Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No | — | —
Fault Major | 187 | MnInpDvcFailOpen | Main/Input Device Failed to Open This condition indicates that the Main/Input Device failed to open when commanded to open. | — | Coast Stop Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No | — | —
Fault Major | 188 | PrchrgDvcFailCls | Precharge Device Failed to Close This condition indicates that the Precharge Device failed to close when commanded to close. | — | Coast Stop Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No | — | —
Fault Major | 189 | PrchrgDvcFailOpn | Precharge Device Failed to Open This condition indicates that the Precharge Device failed to open when commanded to open. | — | Coast Stop Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No | — | —
Fault Major | 190 | MnInpDvc FailCls | Main/Input Device Failed to Close This condition indicates that the Main/Input Device failed to close when commanded to close. | — | Coast Stop Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No | — | —
Fault Major | 191 | MnInpDvcMismatch | Main/Input Device Type Mismatch This condition indicates that the actual Main/Input Device does not match programmed device type. | Check 0:1001 [Main/Inp DvcType]. | Coast Stop Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No | — | —
Fault Major | 192 | PrchrgDvcMismatch | Precharge Device Type Mismatch This condition indicates that the actual Precharge Device does not match programmed device type. | Check 0:1002 [Prchrg Dvc Type]. | Coast Stop Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No | — | —
Fault Major | 193 | OutDvc Open | Output Device Open This condition indicates that the Output Device opened while the drive is running. | — | Coast Stop Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No | — | —
Fault Major | 194 | OutDvc FailClose | Output Device Failed to Close This condition indicates that the Output Device failed to close when commanded to close. | — | Coast Stop Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No | — | —
Fault Major | 195 | OutDvc FailOpen | Output Device Failed to Open This condition indicates that the Output Device failed to open when commanded to open. | — | Coast Stop Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No | — | —
Fault Major | 196 | Out Dvc Mismatch | Output Dvc Type Mismatch This condition indicates that the actual Output Device does not match programmed device type. | Check 0:1005 [Output Dvc Type]. | Coast Stop Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No | — | —
Fault Major | 197 | BypDvc FailClose | Bypass Device Failed to Close This condition indicates that the Bypass Device failed to close when commanded to close. | — | Coast Stop Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No | — | —
Fault Major | 198 | BypDvc FailOpen | Bypass Device Failed to Open This condition indicates that the Bypass Device failed to open when commanded to open. | — | Coast Stop Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No | — | —
Fault Major | 199 | Byp Dvc Mismatch | Bypass Device Type Mismatch This condition indicates that the actual Bypass Device does not match programmed device type. | Check 0:1007 [Bypass Dvc Type]. | Coast Stop Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No | — | —
Fault Major | 285 | Mtr1OutDvc Open | Motor 1 Output Device Open This condition is raised when DeviceLogix detects that the Output Device for Motor 1 is open. | — | Coast Stop Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No | — | —
Fault Major | 286 | Mtr2 OutDvc Open | Motor 2 Output Device Open This condition is raised when DeviceLogix detects that the Output Device for Motor 2 is open. | — | Coast Stop Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No | — | —
Fault Major | 287 | MnInpDvc CfgErr | Main/Input Dvc Configuration Error This condition indicates that 0:1001 [Main/Inp DvcType] has been programmed to be 'NotInstalled' and does not match 0:1000 [Drive Power Cfg]. | — | Coast Stop Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No | — | —
Fault Major | 288 | PrchrgDvc CfgErr | Precharge Dvc Configuration Error This condition indicates that 0:1002 [Prchrg Dvc Type] has been programmed to be 'NotInstalled' and does not match 0:1000 [Drive Power Cfg]. | — | Coast Stop Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No | — | —
Fault Major | 289 | Out Dvc Cfg Err | Output Dvc Configuration Error This condition indicates that 0:1005 [Output DvcType] has been programmed to be 'NotInstalled' and does not match 0:1000 [Drive Power Cfg]. | — | Coast Stop Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No | — | —
Fault Major | 290 | Byp Dvc Cfg Err | Bypass Dvc Configuration Error This condition indicates that 0:1007 [Bypass DvcType] has been programmed to be 'NotInstalled' and does not match 0:1000 [Drive Power Cfg]. | — | Coast Stop Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No | — | —
Fault Major | 291 | VltgDtctdSysTest | Voltage Detected in System Test This condition indicates that Line Voltage is detected in System Test Mode. | — | Coast Stop Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No | — | —
Event | 292 | In SysTest Mode | Drive in System Test Mode This Event is raised when the drive is switched to System Test Mode from Normal Operating Mode. The modes are changed by 0:1025 [DrvOperatingMode]. | — | — | — | —
Event | 293 | In Normal OpMode | Drive in Normal Operating Mode This Event is raised when the drive is switched to Normal Operating Mode from System Test mode. The modes are changed by 0:1025 [DrvOperatingMode]. | — | — | — | —
Resettable Fault | 300 | Nvs Lost Config | Nonvolatile Storage Config File Lost The configuration file that is stored in nonvolatile memory is corrupt. | — | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 7 ‘Board Faults’ | — | —
Non-Resettable Fault | 301 | Pfile Create Err | Profile Creation Error Main control board firmware failed to create a profile for one of the power peripherals. | Cycle power. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Non-Resettable Fault | 302 | Pfile Login Err | Profile Login Error One of the power peripherals has attempted to log in with an invalid ID. | Cycle power. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 303 | HSI Offline | The main control board has lost communication with the fiber interface board (FIB). Can occur during a flash update. | Cycle power. If the fault persists replace main control board. If the fault persists replace FIB. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 305 | No Sfib Detected | No SFIB Detected Main control board firmware failed to connect to the fiber interface board (FIB). | Power down and check the hardware. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Alarm 1 | 306 | HW Not Compatble | Hardware Not Compatble Main control board firmware has found power peripherals (PLI boards, CSBs, and AC precharge modules) that are incompatible. | Power down and check the hardware. | — | — | —
Non-Resettable Fault | 307 | NVS Read Error | NVS Read Error Main control board firmware failed to read non volatile storage memory. | Cycle power. If the fault persists, run a firmware update. | — | — | —
Alarm 2 | 308 | New System | New System Main control board firmware has detected a new configuration of power peripherals. | Examine parameter 0:90 [Cfg Status]. If the new configuration is desirable, accept the configuration in parameter 0:91 [Cfg Acknowledge]. If it is not, power down and examine the configuration and the fiber-optic connections on the fiber interface board (FIB). | — | — | —
Non-Resettable Fault | 309 | Fw Update Fail | Firmware Update Failed The firmware update for a power peripheral has failed. | Rerun firmware update. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Non-Resettable Fault | 310 | Inv sFib Fbr Cfg | Invalid SFIB Fiber Configuration Main control board firmware has detected an invalid connection to the fiber interface board (FIB). | Power down and examine the fiber-optic connections on the fiber interface board (FIB). | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Non-Resettable Fault | 318 | Unknown Device | Unknown Device In System Main control board firmware has detected an unknown backplane option card. | Examine the status indicators on the option cards for errors. Power down and check backplane connections. Reseat option card if needed. See the associated manual of the option card for troubleshooting.
Non-Resettable Fault | 319 | DPI Card Wrg Slt | DPI Card In Wrong Slot Main control board firmware has detected a DPI backplane option board in a non-DPI backplane option slot. Only the lower slots (4, 5, and 6) support DPI. Backplane option cards that require DPI cannot function in slots 7 and 8. | Power down and examine the placement of backplane option cards in the control pod. Review the slot restrictions in the Installation Instructions. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Non-Resettable Fault | 321 | Inv Dev in Cfg | Invalid Device In Configuration Main control board firmware has detected power peripherals (power cells) that are not a valid peripheral type. | Power down and examine the power peripherals and the fiber-optic connections on the Fiber Interface Board (FIB). | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Non-Resettable Fault | 322 | Op Mode Mismth | Operational Mode Mismatch Main control board firmware has detected an operational mode mismatch. | Power down and verify the fiber connections between transceiver boards and power cells are secure. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Non-Resettable Fault | 330 | No SysId Match | No System ID Match The system does not recognize the product type. | Power down and verify fiber-optic connections. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Alarm 2 | 332 | SafetyPortCnflct | Safety Port Conflict Multiple functional safety option modules are installed. A functional safety option module is installed and a 20-750-ATEX option module is also installed with safety configuration switch S1-1 set to on. | — | — | — | —
Alarm 1 | 333 | NVS Write Error | NVS Write Error Main control board firmware has failed to write to non volatile storage (NVS). | Cycle power. | — | — | —
Alarm 2 | 337 | MtrCtrl Mismatch | Motor Control Mode Mismatch The configured and actual motor control mode do not match. The value of parameter 0:66 [Pri MtrCtrl Act] is different than parameter 0:65 [Pri MtrCtrl Mode]. | Review the desired motor control mode. Set parameter 0:65 [Pri MtrCtrl Mode] to the proper value. Cycle power to load the control mode. | — | — | —
Alarm 2 | 338 | App Mismatch | Application Mismatch The configured and actual application mode do not match. The value of parameter 0:71 [Application Act] is different than parameter 0:70 [Application Sel]. | Review the desired application mode. Set parameter 0:70 [Application Sel] to the proper value. Cycle power to load the control mode. | — | — | —
Alarm 2 | 339 | Emb Mismatch | Embedded Logic Mismatch Value of 0:72 [Emb Logic Select] does not match the value of 0:73 [Emb Logic Act] (the configured embedded logic does not match the actual embedded logic). | Power cycle or reset the drive or CBI. | — | — | —
Configurable | 340 | Net IO Fault | The network I/O connection has timed out. This condition can be raised while the I/O connection control source is in run mode or while the control source in idle mode after transitioning from run mode. This condition will close all open explicit messaging connections. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 5 ‘ENET Flts’ | 0:360 [Comm Flt Action] | —
Configurable | 341 | Net Idle Fault | Idle packets were received on the network I/O connection. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 5 ‘ENET Flts’ | 0:361 [Idle Flt Action] | —
Configurable | 342 | Net Msg Fault | Explicit messaging control has timed out. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 5 ‘ENET Flts’ | 0:363 [Msg Flt Action] | —
Non-Resettable Fault | 344 | SafetyInit Error | Safety Initialization Error Safety system failed to initialize due to unexpected discrepancy in detected fiber peripherals. | Cycle power and verify fiber connections/ peripherals. Replace Control Board and/or peripherals with recurrence. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Alarm 2 | 345 | Sec MtrCtrl Chng | Secondary Motor Control Mode Changed The configured and actual secondary motor control mode do not match. The value of parameter 0:68 [Sec MtrCtrl Act] different than parameter 0:67 [Sec MtrCtrl Mode]. | Review the desired secondary motor control mode. Set parameter 0:67 [Sec MtrCtrl Mode] to the proper value. Cycle power to load the control mode. | — | — | —
Alarm 2 | 346 | Invalid DL Cfg | Invalid Datalink Configuration Two or more input datalinks are configured to write to the same target parameter. | Reconfigure one of the from-net datalink parameters to write to a different parameter. | — | — | —
Event | 350 | Net Link 1 Up | Network Link 1 Up The interface established a network link on its ENET1 network port. | — | — | — | —
Event | 351 | Net Link 1 Down | Network Link 1 Down The interface lost the network link on its ENET1 network port. | — | — | — | —
Event | 352 | Net Link 2 Up | Network Link 2 Up The interface established a network link on its ENET2 network port. | — | — | — | —
Event | 353 | Net Link 2 Down | Network Link 2 Down The interface lost the network link on its ENET2 network port. | — | — | — | —
Event | 354 | Net Dup Address | Network Duplicate Address Another device having the same IP address as the interface was detected on the network. | — | — | — | —
Event | 355 | Invalid Net Cfg | Invalid Network Configuration The interface-network address configuration parameters are invalid, or the network address that is provided by the BOOTP or DHCP server is invalid. | — | — | — | —
Event | 356 | BOOTP Response | BOOTP Response The interface received a response to its BOOTP request. | — | — | — | —
Event | 357 | DHCP Response | DHCP Response The interface received a response to its DHCP request. | — | — | — | —
Event | 358 | DHCP Renew | DHCP Renew The interface renewed its network address lease with the DHCP Server. | — | — | — | —
Event | 359 | DHCP Rebind | DHCP Rebind The interface rebinded its network address lease with the DHCP Server. | — | — | — | —
Event | 360 | DHCP Release | DHCP Release The interface network address lease expired. | — | — | — | —
Event | 361 | Net Sent Reset | Net Sent Reset The interface received a reset command from the network. | — | — | — | —
Event | 362 | Net IO Open | Network IO Open The I/O connection from the network to the interface has been opened. | — | — | — | —
Event | 363 | Net IO Idle | Net IO Idle The interface received I/O connection ‘idle’ packets from the network. | — | — | — | —
Event | 364 | Net IO Close | Network IO Close The I/O connection from the network to the interface was closed. | — | — | — | —
Event | 365 | Net IO Timeout | Net IO Timeout The interface I/O connection has timed out. | — | — | — | —
Event | 366 | Net IO Abort | Net IO Abort The interface I/O connection was aborted because the datalink configuration was changed. | — | — | — | —
Event | 367 | PCCC IO Open | PCCC IO Open The interface began receiving PCCC control messages after the PCCC Control Timeout was set to a nonzero value. | — | — | — | —
Event | 368 | PCCC IO Close | PCCC IO Close The device that sends PCCC control messages to the interface (for example, the Control Bar feature in Connected Components Workbench) has set the PCCC Control Timeout to zero. | — | — | — | —
Event | 369 | PCCC IO Timeout | PCCC IO Timeout The interface has not received a PCCC control message before the PCCC Control Timeout. | — | — | — | —
Event | 370 | Msg Ctrl Open | Msg Ctrl Open The timeout attribute in the CIP-based network Assembly Object was set to a nonzero value. This value allows control messages to be sent to the interface via the CIP-based network Assembly Object. | — | — | — | —
Event | 371 | Msg Ctrl Close | Msg Ctrl Close The timeout attribute in the CIP-based network Assembly Object was set to zero. A setting of zero does not allow control messages to be sent to the interface via the CIP-based network Assembly Object. | — | — | — | —
Event | 372 | Msg Ctrl Timeout | Msg Ctrl Timeout The interface has not received a control message via the CIP-based network Assembly Object before the object timeout attribute triggered. | — | — | — | —
Event | 375 | Net Ring Up | Net Ring Up The Device Level Ring (DLR) status is Normal. | — | — | — | —
Event | 376 | Net Ring Down | Net Ring Down The Device Level Ring (DLR) status is Faulted. | — | — | — | —
Fault Major | 377 | Invld SF6kFbrCfg | Invalid SFIB6000 Fiber Config This condition is raised by the start up sequencer when it detects a failure to login by the SFIB. | — | — | — | —
Fault Major | 378 | Invld PCCBFbrCfg | Invalid PCCB Fiber Config This condition is raised by the start up sequencer when it detects that the number of PCCB's that login does not match the number specified in the DHCF. | — | — | — | —
Fault Major | 379 | Invld PIOBFbrCfg | Invalid PIOB Fiber Config This condition is raised by the start up sequencer when it detects a failure to login by the PIOB. | — | — | — | —
Fault Major | 380 | InvldPCCBCurRtng | Invalid PCCB Current Rating This condition is raised by the start up sequencer when it detects that the Power Cell Current Rating specified in the DHCF does not match the Power Cell Current Rating parameter read from PCCB. | — | — | — | —
Fault Major | 381 | Invld PCCBBypOpt | Invalid PCCB Bypass option This condition is raised by the start up sequencer when it detects that the Power Cell Bypass Option specified in the DHCF does not match the Power Cell Bypass Option parameter read from PCCB. | — | — | — | —
Fault Major | 382 | Enc Card Dtctd | Encoder Card Detected This condition is raised by the start up sequencer when it detects an Encoder Card. Power down control power and unplug the card from the Option Backplane. | — | — | — | —
Fault Major | 383 | SafetyCard Dtctd | Safety Card Detected This condition is raised by the start up sequencer when it detects a Safety Card. Power down control power and unplug the card from the Option Backplane. | — | — | — | —
Fault Major | 384 | UFB Dtctd | UFB Detected This condition is raised by the start up sequencer when it detects a Universal Feedback Card (UFB). Power down control power and unplug the card from the Option Backplane. | — | — | — | —
Fault Major | 385 | Pre Charge Fail | Pre Charge Fail This condition is raised by the firmware if the precharge sequence is not completed within 15 seconds of being initiated. | — | Additional Fault Action Emergency override response: 0:455 [Emerg Prot OVRD] bit 1 ‘LS Pwr Flts’ | — | —
Fault Major | 386 | DHCFPreProcFail | DHCFPreProcFail This condition indicates a failure in DHCF pre processing function. | — | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault Major | 387 | DHCFPostProcFail | DHCFPostProcFail This condition indicates a failure in DHCF post processing function. | — | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault Major | 388 | Invld DHCF Data | Invld DHCF Data This condition indicates that data read from the DHCF is not within the limits expected by the drive firmware. | — | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Alarm 1 | 389 | Fan 10 Life | Fan 10 Life Elapsed life of the VFD Cabinet fans has exceeded the expected total life. | Replace VFD Cabinet fans and reset the Predictive Maintenance function for them. | — | — | —
Alarm 1 | 390 | Fan 11 Life | Fan 11 Life Elapsed life of the VFD Cabinet fans has exceeded the expected total life. | Replace VFD Cabinet fans and reset the Predictive Maintenance function for them. | — | — | —
Alarm 1 | 391 | Fan 12 Life | Fan 12 Life Elapsed life of the VFD Cabinet fans has exceeded the expected total life. | Replace VFD Cabinet fans and reset the Predictive Maintenance function for them. | — | — | —
Alarm 1 | 392 | Fan 13 Life | Fan 13 Life Elapsed life of the VFD Cabinet fans has exceeded the expected total life. | Replace VFD Cabinet fans and reset the Predictive Maintenance function for them. | — | — | —
Alarm 1 | 393 | Fan 21 Life | Fan 21 Life Elapsed life of the Power Cell fans has exceeded the expected total life. | Replace Power Cell fans and reset the Predictive Maintenance function for them. | — | — | —
Alarm 1 | 394 | Fan 22 Life | Fan 22 Life Elapsed life of the Power Cell fans has exceeded the expected total life. | Replace Power Cell fans and reset the Predictive Maintenance function for them. | — | — | —
Alarm 1 | 395 | Fan 23 Life | Fan 23 Life Elapsed life of the Power Cell fans has exceeded the expected total life. | Replace Power Cell fans and reset the Predictive Maintenance function for them. | — | — | —
Alarm 1 | 396 | Fan 24 Life | Fan 24 Life Elapsed life of the Power Cell fans has exceeded the expected total life. | Replace Power Cell fans and reset the Predictive Maintenance function for them. | — | — | —
Alarm 1 | 397 | Fan 25 Life | Fan 25 Life Elapsed life of the Power Cell fans has exceeded the expected total life. | Replace Power Cell fans and reset the Predictive Maintenance function for them. | — | — | —
Alarm 1 | 398 | Fan 26 Life | Fan 26 Life Elapsed life of the Power Cell fans has exceeded the expected total life. | Replace Power Cell fans and reset the Predictive Maintenance function for them. | — | — | —
Alarm 1 | 399 | Fan 27 Life | Fan 27 Life Elapsed life of the Power Cell fans has exceeded the expected total life. | Replace Power Cell fans and reset the Predictive Maintenance function for them. | — | — | —
Alarm 1 | 400 | Fan 28 Life | Fan 28 Life Elapsed life of the Power Cell fans has exceeded the expected total life. | Replace Power Cell fans and reset the Predictive Maintenance function for them. | — | — | —
Alarm 1 | 401 | Fan 29 Life | Fan 29 Life Elapsed life of the Power Cell fans has exceeded the expected total life. | Replace Power Cell fans and reset the Predictive Maintenance function for them. | — | — | —
Alarm 1 | 402 | Fan 31 Life | Fan 31 Life Elapsed life of the Transformer Cabinet fans has exceeded the expected total life. | Replace Transformer Cabinet fans and reset the Predictive Maintenance function for them. | — | — | —
Alarm 1 | 403 | Fan 32 Life | Fan 32 Life Elapsed life of the Transformer Cabinet fans has exceeded the expected total life. | Replace Transformer Cabinet fans and reset the Predictive Maintenance function for them. | — | — | —
Alarm 1 | 404 | Fan 33 Life | Fan 33 Life Elapsed life of the Transformer Cabinet fans has exceeded the expected total life. | Replace Transformer Cabinet fans and reset the Predictive Maintenance function for them. | — | — | —
Alarm 1 | 405 | Fan 34 Life | Fan 34 Life Elapsed life of the Transformer Cabinet fans has exceeded the expected total life. | Replace Transformer Cabinet fans and reset the Predictive Maintenance function for them. | — | — | —
Alarm 1 | 406 | Fan 35 Life | Fan 35 Life Elapsed life of the Transformer Cabinet fans has exceeded the expected total life. | Replace Transformer Cabinet fans and reset the Predictive Maintenance function for them. | — | — | —
Alarm 1 | 407 | Fan 36 Life | Fan 36 Life Elapsed life of the Transformer Cabinet fans has exceeded the expected total life. | Replace Transformer Cabinet fans and reset the Predictive Maintenance function for them. | — | — | —
Alarm 1 | 408 | Fan 37 Life | Fan 37 Life Elapsed life of the Transformer Cabinet fans has exceeded the expected total life. | Replace Transformer Cabinet fans and reset the Predictive Maintenance function for them. | — | — | —
Alarm 1 | 409 | Fan 38 Life | Fan 38 Life Elapsed life of the Transformer Cabinet fans has exceeded the expected total life. | Replace Transformer Cabinet fans and reset the Predictive Maintenance function for them. | — | — | —
Alarm 1 | 410 | Fan 39 Life | Fan 39 Life Elapsed life of the Transformer Cabinet fans has exceeded the expected total life. | Replace Transformer Cabinet fans and reset the Predictive Maintenance function for them. | — | — | —
Alarm 1 | 411 | Fan 40 Life | Fan 40 Life Elapsed life of the Transformer Cabinet fans has exceeded the expected total life. | Replace Transformer Cabinet fans and reset the Predictive Maintenance function for them. | — | — | —
Alarm 1 | 412 | Fan 71 Life | Fan 71 Life Elapsed life of the optional Filter Cabinet fans has exceeded the expected total life. | Replace optional Filter Cabinet fans and reset the Predictive Maintenance function for them. | — | — | —
Alarm 1 | 413 | Fan 72 Life | Fan 72 Life Elapsed life of the optional Filter Cabinet fans has exceeded the expected total life. | Replace optional Filter Cabinet fans and reset the Predictive Maintenance function for them. | — | — | —
Alarm 1 | 414 | PrevMnt Schedule | Drive Preventative Maintenance This condition indicates that a Preventative Maintenance schedule is due for the drive. | Check the value of parameter 0:7 [Elpsed Run Time], then see the PowerFlex® 6000T Drives Hardware Service Manual, publication 6000-TG100. | — | — | —
Alarm 1 | 417 | Rplc PodFan1-90d | Replace PodFan1 in 90days This condition indicates that the specified Fan needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 418 | Rplc PodFan2-90d | Replace PodFan2 in 90days This condition indicates that the specified Fan needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 419 | Rplc PodFan3-90d | Replace PodFan3 in 90days This condition indicates that the specified Fan needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 420 | RplcDoorFan1-90d | Replace DoorFan1 in 90days This condition indicates that the specified Fan needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 421 | RplcDoorFan2-90d | Replace DoorFan2 in 90days This condition indicates that the specified Fan needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 422 | RplcDoorFan3-90d | Replace DoorFan3 in 90days This condition indicates that the specified Fan needs to be replaced within 90 days. | — | — | — | —
Event | 423 | PodFan1TimeChngd | Pod Fan 1 Run Time Changed This event indicates that the user changed the Run Time value for the specified cooling fan. | — | — | — | —
Event | 424 | PodFan2TimeChngd | Pod Fan 2 Run Time Changed This event indicates that the user changed the Run Time value for the specified cooling fan. | — | — | — | —
Event | 425 | PodFan3TimeChngd | Pod Fan 3 Run Time Changed This event indicates that the user changed the Run Time value for the specified cooling fan. | — | — | — | —
Event | 426 | DoorF1TimeChngd | Door Fan 1 Run Time Changed This event indicates that the user changed the Run Time value for the specified cooling fan. | — | — | — | —
Event | 427 | DoorF2TimeChngd | Door Fan 2 Run Time Changed This event indicates that the user changed the Run Time value for the specified cooling fan. | — | — | — | —
Event | 428 | DoorF3TimeChngd | Door Fan 3 Run Time Changed This event indicates that the user changed the Run Time value for the specified cooling fan. | — | — | — | —
Event | 429 | DoorPdFanRplcAck | Door Pod Fan Replacement Ack This event indicates that the user has acknowledged the Door or Pod Fan replacement alarm. | — | — | — | —
Alarm 1 | 430 | Pod Fan 2 Life | Pod Fan 2 Life This condition indicates that the Elapsed life of the specified Pod fan has exceeded the expected total life. | Replace fan and reset the Predictive Maintenance function for them. | — | — | —
Alarm 1 | 431 | Pod Fan 3 Life | Pod Fan 3 Life This condition indicates that the Elapsed life of the specified Pod fan has exceeded the expected total life. | Replace fan and reset the Predictive Maintenance function for them. | — | — | —
Alarm 1 | 432 | Door Fan 1 Life | Door Fan 1 Life This condition indicates that the Elapsed life of the specified Pod fan has exceeded the expected total life. | Replace fan and reset the Predictive Maintenance function for them. | — | — | —
Alarm 1 | 433 | Door Fan 2 Life | Door Fan 2 Life This condition indicates that the Elapsed life of the specified Pod fan has exceeded the expected total life. | Replace fan and reset the Predictive Maintenance function for them. | — | — | —
Alarm 1 | 434 | Door Fan 3 Life | Door Fan 3 Life This condition indicates that the Elapsed life of the specified Pod fan has exceeded the expected total life. | Replace fan and reset the Predictive Maintenance function for them. | — | — | —
Alarm 1 | 435 | Pod Fan 1 Life | Pod Fan 1 Life This condition indicates that the Elapsed life of the specified Pod fan has exceeded the expected total life. | Replace fan and reset the Predictive Maintenance function for them. | — | — | —
Alarm 1 | 436 | Tx1PdMCalc Invld | Transformer 1 Cabinet PM Calc Invalid This condition indicates that the predictive maintenance calculation for specified cabinet is invalid due to loss of temperature sensor. | Check if the temperature range is outside the expected range (-20…+100 °C). Check if the sensor is faulty. If an RTD Channel Error occurs along with this error, investigate and resolve the channel error first. | — | — | —
Alarm 1 | 437 | Tx2PdMCalc Invld | Transformer 2 Cabinet PM Calc Invalid This condition indicates that the predictive maintenance calculation for specified cabinet is invalid due to loss of temperature sensor. | Check if the temperature range is outside the expected range (-20…+100 °C). Check if the sensor is faulty. If an RTD Channel Error occurs along with this error, investigate and resolve the channel error first. | — | — | —
Alarm 1 | 438 | PcPdMCalc Invld | Power Cell Cabinet PM Calc Invalid This condition indicates that the predictive maintenance calculation for specified cabinet is invalid due to loss of temperature sensor. | Check if the temperature range is outside the expected range (-20…+100 °C). Check if the sensor is faulty. If an RTD Channel Error occurs along with this error, investigate and resolve the channel error first. | — | — | —
Alarm 1 | 439 | FilPdMCalc Invld | Filter Cabinet PM Calc Invalid This condition indicates that the predictive maintenance calculation for specified cabinet is invalid due to loss of temperature sensor. | Check if the temperature range is outside the expected range (-20…+100 °C). Check if the sensor is faulty. If an RTD Channel Error occurs along with this error, investigate and resolve the channel error first. | — | — | —
Alarm 1 | 440 | VFDPdMCalc Invld | VFD Cabinet PM Calc Invalid This condition indicates that the predictive maintenance calculation for specified cabinet is invalid due to loss of temperature sensor. | Check if the temperature range is outside the expected range (-20…+100 °C). Check if the sensor is faulty. If an RTD Channel Error occurs along with this error, investigate and resolve the channel error first. | — | — | —
Resettable Fault | 103 | Device Timeout | Device Message Timeout The main control board has detected that one of the power peripherals (PLI, CSB, or precharge board) has stopped transmitting messages. | Power down and then check the fiber-optic communication connections. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 200 | Image Wtchdg | Image Watchdog Fault A power peripheral (PIOB or SFIB) has detected that the main control board has stopped transmitting for 10 milliseconds. | Power down and then check the fiber-optic communication connections. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Non-Resettable Fault | 201 | Const Inv Flt | Constants Message Invalid Fault The constants header information did not match the content expected by the power peripheral (PIOB or PCCB). | Cycle power. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Non-Resettable Fault | 202 | Const Chksum Flt | Constants Checksum Fault The constants download failed the checksum check by the power peripheral (PIOB or PCCB). | Cycle power. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 203 | Fiber Offline 0 | Fiber online to offline 0 The fiber-optic communication link between the main control board and PCCB U0 transitioned from online to offline. | Clear faults. If this fault persists, power down and then check the fiber-optic communication connections. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 204 | Fiber Offline 1 | Fiber online to offline 1 The fiber-optic communication link between the main control board and PCCB V0 transitioned from online to offline. | Clear faults. If this fault persists, power down and then check the fiber-optic communication connections. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 205 | Fiber Offline 2 | Fiber online to offline 2 The fiber-optic communication link between the main control board and PCCB W0 transitioned from online to offline. | Clear faults. If this fault persists, power down and then check the fiber-optic communication connections. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 206 | Fiber Offline 3 | Fiber online to offline 3 The fiber-optic communication link between the main control board and PCCB U1 transitioned from online to offline. | Clear faults. If this fault persists, power down and then check the fiber-optic communication connections. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 207 | Fiber Offline 4 | Fiber online to offline 4 The fiber-optic communication link between the main control board and PCCB V1 transitioned from online to offline. | Clear faults. If this fault persists, power down and then check the fiber-optic communication connections. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 208 | Fiber Offline 5 | Fiber online to offline 5 The fiber-optic communication link between the main control board and PCCB W1 transitioned from online to offline. | Clear faults. If this fault persists, power down and then check the fiber-optic communication connections. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 209 | Fiber Offline 6 | Fiber online to offline 6 The fiber-optic communication link between the main control board and PCCB U2 transitioned from online to offline. | Clear faults. If this fault persists, power down and then check the fiber-optic communication connections. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 210 | Fiber Offline 7 | Fiber online to offline 7 The fiber-optic communication link between the main control board and PCCB V2 transitioned from online to offline. | Clear faults. If this fault persists, power down and then check the fiber-optic communication connections. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 211 | Fiber Offline 8 | Fiber online to offline 8 The fiber-optic communication link between the main control board and PCCB W2 transitioned from online to offline. | Clear faults. If this fault persists, power down and then check the fiber-optic communication connections. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 212 | Fiber Offline 9 | Fiber online to offline 9 The fiber-optic communication link between the main control board and PCCB U3 transitioned from online to offline. | Clear faults. If this fault persists, power down and then check the fiber-optic communication connections. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 213 | Fiber Offline 10 | Fiber online to offline 10 The fiber-optic communication link between the main control board and PCCB V3 transitioned from online to offline. | Clear faults. If this fault persists, power down and then check the fiber-optic communication connections. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 214 | Fiber Offline 11 | Fiber online to offline 11 The fiber-optic communication link between the main control board and PCCB W3 transitioned from online to offline. | Clear faults. If this fault persists, power down and then check the fiber-optic communication connections. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 215 | Fiber Offline 12 | Fiber online to offline 12 The fiber-optic communication link between the main control board and PCCB U4 transitioned from online to offline. | Clear faults. If this fault persists, power down and then check the fiber-optic communication connections. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 216 | Fiber Offline 13 | Fiber online to offline 13 The fiber-optic communication link between the main control board and PCCB V4 transitioned from online to offline. | Clear faults. If this fault persists, power down and then check the fiber-optic communication connections. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 217 | Fiber Offline 14 | Fiber online to offline 14 The fiber-optic communication link between the main control board and PCCB W4 transitioned from online to offline. | Clear faults. If this fault persists, power down and then check the fiber-optic communication connections. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 218 | Fiber Offline 15 | Fiber online to offline 15 The fiber-optic communication link between the main control board and PCCB U5 transitioned from online to offline. | Clear faults. If this fault persists, power down and then check the fiber-optic communication connections. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 219 | Fiber Offline 16 | Fiber online to offline 16 The fiber-optic communication link between the main control board and PCCB V5 transitioned from online to offline. | Clear faults. If this fault persists, power down and then check the fiber-optic communication connections. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 220 | Fiber Offline 17 | Fiber online to offline 17 The fiber-optic communication link between the main control board and PCCB W5 transitioned from online to offline. | Clear faults. If this fault persists, power down and then check the fiber-optic communication connections. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 221 | Fiber Offline 18 | Fiber online to offline 18 The fiber-optic communication link between the main control board and PCCB U6 transitioned from online to offline. | Clear faults. If this fault persists, power down and then check the fiber-optic communication connections. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 222 | Fiber Offline 19 | Fiber online to offline 19 The fiber-optic communication link between the main control board and PCCB V6 transitioned from online to offline. | Clear faults. If this fault persists, power down and then check the fiber-optic communication connections. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 223 | Fiber Offline 20 | Fiber online to offline 20 The fiber-optic communication link between the main control board and PCCB W6 transitioned from online to offline. | Clear faults. If this fault persists, power down and then check the fiber-optic communication connections. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 224 | Fiber Offline 21 | Fiber online to offline 20 The fiber-optic communication link between the main control board and PCCB U7 transitioned from online to offline. | Clear faults. If this fault persists, power down and then check the fiber-optic communication connections. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 225 | HSI Offline 0 | HSI online to offline 0 The fiber interface board (FIB) has lost communication with the main control board. This fault concerns the fiber-optic connections to the motor side inverter. Can occur during a firmware update. | Cycle power. If the fault persists replace main control board. If the fault persists replace FIB. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 226 | HSI Offline 1 | HSI online to offline 1 The fiber interface board (FIB) has lost communication with the main control board. This fault concerns the fiber-optic connections to the line side converter. Can occur during a firmware update. | Cycle power. If the fault persists replace main control board. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Alarm 1 | 227 | Over Temp Alarm | Board OT Alarm The temperature of the fiber interface board (FIB) has exceeded the Alarm Temperature (75 °C). Possible causes include high ambient temperature and obstructed airflow. | Check the ambient temperature. Check the condition of cabinet air filters. | — | — | —
Resettable Fault | 228 | Over Temp Fault | Board OT Fault The temperature of the fiber interface board (FIB) has exceeded the Fault Temperature (80 °C). Possible causes include high ambient temperature and obstructed airflow. | Check the ambient temperature. Check the condition of cabinet air filters. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Alarm 1 | 229 | Under Temp Alarm | Board UT Alarm The temperature of the fiber interface board (FIB) has fallen below the Alarm Temperature (-25 °C). Possible causes include low ambient temperature and obstructed airflow. | Check the ambient temperature. Check the condition of cabinet air filters. | — | — | —
Resettable Fault | 230 | Under Temp Fault | Board UT Fault The temperature of the fiber interface board (FIB) has fallen below the Fault Temperature (-30 °C). Possible causes include low ambient temperature and obstructed airflow. | Check the ambient temperature. Check the condition of cabinet air filters. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Alarm 1 | 267 | Flash Timeout | HSI Flash Timeout A peripheral device update time-out has happened with the main control board during a firmware update. Port number of attached device is the first two digits of the fault/alarm code. | — | — | — | —
Alarm 1 | 268 | FlashRst Timeout | HSI Flash Reset Timeout A peripheral device update reset time-out has happened with the main control board during a firmware update. Port number of attached device is the first two digits of the fault/alarm code. | — | — | — | —
Alarm 1 | 269 | Login Timeout | HSI Login Timeout A peripheral device login with the main control board failed after firmware update. Port number of attached device is the first two digits of the fault/alarm code. | — | — | — | —
Alarm 1 | 270 | Flash DPI Error | Flash DPI Error A peripheral device DPI error has occurred during a firmware update. Port number of attached device is the first two digits of the fault/ alarm code. | — | — | — | —
Resettable Fault | 272 | Fiber Offline 22 | Fiber online to offline 22 The fiber-optic communication link between the main control board and PCCB V7 transitioned from online to offline. | Clear faults. If this fault persists, power down and then check the fiber-optic communication connections. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 273 | Fiber Offline 23 | Fiber online to offline 23 The fiber-optic communication link between the main control board and PCCB W7 transitioned from online to offline. | Clear faults. If this fault persists, power down and then check the fiber-optic communication connections. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 274 | Fiber Offline 24 | Fiber online to offline 24 The fiber-optic communication link between the main control board and PCCB U8 transitioned from online to offline. | Clear faults. If this fault persists, power down and then check the fiber-optic communication connections. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 275 | Fiber Offline 25 | Fiber online to offline 25 The fiber-optic communication link between the main control board and PCCB V8 transitioned from online to offline. | Clear faults. If this fault persists, power down and then check the fiber-optic communication connections. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 276 | Fiber Offline 26 | Fiber online to offline 26 The fiber-optic communication link between the main control board and PCCB W8 transitioned from online to offline. | Clear faults. If this fault persists, power down and then check the fiber-optic communication connections. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 277 | PIOBFbrOffline 0 | PIOB Fiber Online to Offline 0 The fiber-optic communication link between the main control board and PIOB Inv transitioned from online to offline. | Clear faults. If this fault persists, power down and then check the fiber-optic communication connections. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 278 | PIOBFbrOffline 1 | PIOB Fiber Online to Offline 1 The fiber-optic communication link between the main control board and PIOB Conv transitioned from online to offline. | Clear faults. If this fault persists, power down and then check the fiber-optic communication connections. | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 279 | FdbkMsg PIOBFbr0 | Feedback Msg Timeout PIOB Fiber 0 This condition is raised when the drive detects loss of feedback message from PIOB Inv. | Clear faults. If this fault persists, power down and then check the fiber-optic communication connections. | Coast (Motor Side Inverter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 280 | FdbkMsg PIOBFbr1 | Feedback Msg Timeout PIOB Fiber 1 This condition is raised when the drive detects loss of feedback message from PIOB Conv. | Clear faults. If this fault persists, power down and then check the fiber-optic communication connections. | Coast (Motor Side Inverter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 281 | CtrlMsgWdog Tout | Control Msg Watchdog Timeout The watch dog timer for transmission of the Control Message between the main control board and SFIB has timed-out. | Power down and then check the fiber-optic communication connections. If it recurs, replace the main control board. If it continues to recur, consult the factory. | Coast (Motor Side Inverter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 7 ‘Board Faults’ | — | —
Resettable Fault | 282 | System Reset Flt | System Reset Fault This condition indicates that a System Reset is received in the System Command message via HSI. | — | Coast (Motor Side Inverter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 7 ‘Board Faults’ | — | —
Resettable Fault | 283 | Power Down Fault | Power Down Fault This condition is a Major Fault and indicates that the SFIB FPGA received a 24V Voltage Monitor fault while the drive is running. | — | Coast (Motor Side Inverter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 7 ‘Board Faults’ | — | —
Event | 284 | Power Down SFIB | Power Down SFIB This condition is an Event and indicates that the SFIB FPGA received a 24V Voltage Monitor fault while the drive is not running. | — | — | — | —
Resettable Fault | 294 | SFIB FPGA HW | SFIB FPGA HW Fault This condition is a Major Fault and indicates that the SFIB FPGA has detected a HW fault. | Check P97 and P98 in Port 0 diagnostics to see the fault bits. | Coast (Motor Side Inverter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 7 ‘Board Faults’ | — | —

## Port 9
Condition Type | Condition Code | Display Text | Fault | Action | Fault Action | Configuration Parameter | Configurable Action
none | 0 | No Entry
Alarm 2 | 1 | DLX Runtime Err | DeviceLogix Runtime Error The DeviceLogix program has encountered an error with the operation of runtime logic. | Consult the DeviceLogix editor for specific error and error details. | — | — | —
Configurable | 2 | DLX IO Cfg Invld | DLX IO Configuration Invalid One or more parameters used by the DeviceLogix program do not exist on the port specified in the program mapping file. | Install option modules in the slots expected by the DeviceLogix program or update the DeviceLogix program to accommodate the existing option module configuration. | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 6 ‘DevLgx Flts’ | 9:1003 [DLX InvldIO Actn] | —
Resettable Fault | 3 | DLX Checksum | DeviceLogix Checksum DeviceLogix storage checksum failed. Data set to default values. | — | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 6 ‘DevLgx Flts’ | — | —
Resettable Fault | 4 | EmbLogic Adapter | Embedded Logic Adapter The DeviceLogix adapter has a fault. | — | Coast (Motor Side Inverter) Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 6 ‘DevLgx Flts’ | — | —
Alarm 2 | 12 | TP MtrCtrl Mode | Torque Prove Motor Control Mode Conflict The torque proving application has been selected with an unsupported motor control mode. The product is prevented from running in this configuration. | To clear this alarm, change the value of parameter 0:65 [Pri MtrCtrl Mode] to an induction motor control mode or change the value of parameter 0:70 [Application Sel] to a value other than torque proving. | — | — | —
Alarm 2 | 13 | Torq Prove Cflct | Torque Prove Conflict When parameter 10:50 [Trq Prove Cfg] is enabled, parameter 10:65 [Pri MtrCtrl Mode] must be properly set, and parameters 10:1000 [Pri Vel Fb Sel] and 10:1013 [PReg Fb Sel] must be set to a valid feedback device (does not have to be the same device, and Open Loop and Simulation Feedback are not considered valid feedback devices). Parameter 0:75 [Mtr Ctrl Sel Act] must indicate primary motor control mode. If these parameters point to a feedback module, the module parameters must also be properly set. On the module, the feedback loss action CANNOT be set to 0 'Ignore'. Does not work in PM FV mode. Does not work with single ended or channel A only encoders. | Correct the parameter configuration. | — | — | —
Minor Fault | 14 | TP Encls Config | Torque Prove Encoderless Configuration Encoderless TorqProve has been enabled but user has not read and understood application concerns of encoderless operation. | — | — | — | —
Minor Fault | 15 | TP Sec Mtr Ctrl | Torque Prove Secondary Motor Control Conflict Torque proving has been enabled but the user has not read and understood the application concerns related to configuration of the secondary motor control port. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 9 ‘TorqPrv Flts’ | — | —
Alarm 2 | 16 | PID MtrCtrl Port | PID Motor Control Port Configuration Parameter 9:25 [PID Ref Sel], 9:35 [PID Fdbk Sel], 9:42 [PID FBLoss SpSel], or 9:43 [PID FBLoss TqSel] is configured for a data source that resides in a motor control port that is not selected in parameter 9:16 [PID Mtr Ctrl Sel]. | Change the value of parameter 9:16 [PID Mtr Ctrl Sel] or reconfigure parameter 9:25 [PID Ref Sel], 9:35 [PID Fdbk Sel], 9:42 [PID FBLoss SpSel], and 9:43 [PID FBLoss TqSel] to eliminate selection of data sources in the motor control port that is not selected in parameter 9:16 [PID Mtr Ctrl Sel]. | — | — | —
Alarm 2 | 48 | Sleep Config | Sleep Configuration There is a Sleep/Wake configuration error. With Sleep Wake Mode = Direct, possible causes include: Drive is stopped and Wake Level < Sleep Level. | Stop = CF, Run, Run Fwd, or Run Rev is not configured in Digital Input functions. | — Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: N/A Emergency override response: Cannot override this fault. | — | —
Alarm 1 | 49 | Waking | Waking The Wake timer is counting toward a value (parameter 9:95 [Wake Time]) that starts the drive. | Normal operation that indicates that the drive is waking and is about to start. | — | — | —
Alarm 2 | 50 | SleepMtrCtrl Cfg | Sleep/Wake Motor Control Configuration Error A motor control mode is configured for the secondary motor control port (port 11) while the sleep/wake feature is enabled. The product only supports sleep/wake as a standalone application with the primary motor control port (port 10). | Set 0:67 [Sec MtrCtrl Mode] to 0 'None' or set 9:90 [Sleep Wake Mode] to 0 'Disabled'. | — | — | —

## Port 10-11
Condition Type | Condition Code | Display Text | Fault | Action | Fault Action | Configuration Parameter | Configurable Action
none | 0 | No Entry
Configurable | 1 | Power Loss | Power Loss The DC bus voltage remained below the power loss level for longer than power loss time. | Possible causes include interruption of incoming AC power at the line side converter. See parameters 10:272 [Pwr Loss A Level], 10:273 [Pwr Loss A Time], 10:276 [Pwr Loss B Level] and 10:277 [Pwr Loss B Time]. | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 2 ‘MS Ctrl Flts’ | 10:270 [Power Loss Actn] | —
Alarm 1 | 2 | Mtr Ovrld Alarm | Motor Overload Alarm Value of parameter 10:207 [Mtr OL Counts] exceeds the value of parameter 10:202 [Mtr OL Alm Level]. | — | — | — | —
Configurable | 3 | Motor Overload | Motor Overload An internal (software model) motor overload trip has occurred. | See parameters 10:3 [Output Current], 10:401 [Motor NP Amps, 10:203 [Mtr OL Factor], and/or 10:204 [Mtr OL Hertz]. | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 2 ‘MS Ctrl Flts’ | 10:200 [Mtr OL Action] | —
Configurable | 4 | Load Loss | Load Loss The output torque current is below the value that is programmed in parameter 10:251 [Load Loss Level] for a time period greater than the time programmed in parameter 10:252 [Load Loss Time]. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 2 ‘MS Ctrl Flts’ | 10:250 [Load Loss Action] | —
Resettable Fault | 7 | TorqPrv Spd Band | Torque Prove Speed Band The difference between parameter 10:1914 [VRef Commanded] and parameter 10:1044 [Motor Vel Fb] has exceeded the level in parameter 9:54 [Speed Dev Band] for a time period greater than the time programmed in parameter 9:55 [SpdBand Intgrtr]. | Increase parameter 10:906 [System BW] or parameter 9:54 [Speed Dev Band] and parameter 9:55 [SpdBand Intgrtr] | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 9 ‘TorqPrv Flts’ | — | —
Configurable | 8 | Output PhaseLoss | Output Phase Loss Current was lost or remained below the threshold set in parameter 10:257 [Out PhaseLossLvl] for 1 second in one or more phases. Decrease the threshold to make the drive less sensitive to trip. This adjustment is necessary when the motor is smaller than the drive rating. If TorqProve™ is active, the current was lost or remained below a threshold for 5 ms. The phases are checked at start to deliver torque to the load. If the drive is faulting on start, increase parameter 10:433 [u FluxUpTime]. If TorqProve is active, and the brake is slipping, this fault occurs. When TorqProve is used, before the signal to the brake is applied to release it, the flux up time is used to check the three phases. The angle is adjusted to deliver current through all three phases. If the motor moves during this test, the brake is not holding and a phase loss can occur. If TorqProve is active, and no brake is present, this fault occurs. Check for an open output contactor. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 2 ‘MS Ctrl Flts’ | 10:256 [OutPhaseLossA ctn] | —
Configurable | 9 | Decel Inhibit | Decel Inhibit The drive is not following the commanded deceleration ramp because it is attempting to limit DC bus voltage. When using non-vector (scalar) control modes on high inertia loads, set parameter 10:490 [u Slip RPM atFLA] to 0. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 2 ‘MS Ctrl Flts’ | 10:170 [Dec Inhibit Actn] | —
Resettable Fault | 10 | OverSpeed Limit | OverSpeed Limit Motor speed has exceeded the limit set by parameter 10:1904 [Overspeed Limit]. For forward motor rotation, this limit is parameter 10:1898 [Vel Limit Pos] + parameter 10:1904 [Overspeed Limit]. For reverse motor rotation, this limit is parameter 10:1899 [Vel Limit Neg] - parameter 10:1904 [Overspeed Limit]. When flux vector control is selected, parameter 10:1042 [Vel Fb Active] determines the motor operating speed. For all other control modes, parameter 10:1 [Output Frequency] determines the motor operating speed. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 2 ‘MS Ctrl Flts’ | — | —
Alarm 1 | 11 | BrakeSlippedActv | Brake Slipped - Drive Active For TorqProve only. The encoder movement has exceeded the level in parameter 9:63 [Brk Slip Thresh] after the brake was set and the brake slip maneuver is controlling the drive (the drive is active). Cycle power to the drive to reset. | Verify mechanical brake function. Increase parameter 9:63 [Brk Slip Thresh] if needed. | — | — | —
Alarm 2 | 12 | BrakeSlippedStop | Brake Slipped - Drive Stopped For TorqProve only. The encoder movement has exceeded the level in parameter 9:63 [Brk Slip Thresh] after the brake was set and the brake slip maneuver is finished (drive is stopped). Cycle power to the drive to reset. | Verify mechanical brake function. Increase parameter 9:63 [Brk Slip Thresh] if needed. | — | — | —
Configurable | 25 | Shear Pin 1 | Shear Pin 1 value exceeded The Shear Pin function has tripped on first pin. Motor current has exceeded the value in parameter 10:243 [Shear Pin1 Level]. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 2 ‘MS Ctrl Flts’ | 10:242 [Shear Pin 1 Actn] | —
Configurable | 26 | Shear Pin 2 | Shear Pin 2 value exceeded The Shear Pin function has tripped on second pin. Motor current has exceeded the value in parameter 10:246 [Shear Pin2 Level]. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 2 ‘MS Ctrl Flts’ | 10:245 [Shear Pin 2 Actn] | —
Alarm 1 | 27 | Drive OverLoad | Drive OverLoad Parameter 10:357 [Drive OL Count] has exceeded 50% but is less than 100%. | — | — | — | —
Resettable Fault | 28 | Drive OverLoad | Drive OverLoad Parameter 10:357 [Drive OL Count] has exceeded 100%. Possible causes include loads that require too much current and power, improper derating for temperature and altitude, and obstructed airflow. | Verify that the drive is sized and derated correctly. Check the condition of cabinet air filters. | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Resettable Fault | 29 | Stator Res Range | Stator Resistance Range Parameter 10:910 [Autotune] is set to 2 ‘Static MtrID’ or 3 ‘Rotate MtrID’ and the value for stator resistance in parameter 10:512 [u IM Stator Res] measured by the Autotune function is not in the range of acceptable values. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 30 | FluxAmpsRef Rang | Flux Amps Reference Range Parameter 10:910 [Autotune] is set to 2 ‘Static MtrID’ or 3 ‘Rotate MtrID’ and the value for flux amps in parameter 10:518 [u Flux Cur Ref] measured by the Autotune function exceeds the value that is programmed in parameter 10:401 [Motor NP Amps]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 31 | Excessive Load | Excessive Load The motor did not come up to speed in the allotted time during Autotune. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 2 ‘MS Ctrl Flts’ | — | —
Resettable Fault | 32 | AutoTune Aborted | Auto Tune Aborted The Autotune function was interrupted. This interruption was the result of manual cancellation or a fault. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 33 | Leakage L Range | Leakage Inductance Range Parameter 10:910 [Autotune] is set to 2 ‘Static MtrID’ or 3 ‘Rotate MtrID’ and the voltage that was measured for motor inductive impedance exceeds 25% of the value of parameter 10:400 [Motor NP Volts]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 38 | Auto Tach Switch | Auto Tach Switch Either of the two following conditions exists: 1. The automatic feedback (tach) switch has occurred and alternate feedback device has failed. 2. The tach switch has not occurred, Auto Tach Switch Option is enabled and both primary and alternate devices have failed. | Investigate feedback device failure. | Coast (Motor Side Inverter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 8 ‘Fdbk Faults’ | 10:1019 [Fb Loss Action] | —
Alarm 1 | 39 | Start On PowerUp | Start On PowerUp When 10/11:50 [Start At PowerUp] is enabled, an alarm will be set for the time programmed in 10/11:52 [PowerUp Delay]. | — | — | — | —
Resettable Fault | 43 | Autn Enc Angle | Autotune Encoder Angle Parameter 10:521 [u EncLs AngCmp] is out of range. | — | Coast (Motor Side Inverter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 44 | Autn Vel Rstrct | Autotune Velocity Restricted Velocity Command is too low to complete the inertia test. This condition is applicable to induction, surface permanent magnet, and interior permanent magnet motors. | — | Coast (Motor Side Inverter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: N/A | — | —
Resettable Fault | 45 | Autotune CurReg | Autotune Current Regulator Calculated value for the current regulator integral gain is out of range. | Verify motor nameplate data. Check motor connections. Rerun autotune. If condition persists, modify the value of parameter 10:450 [VCL CReg Damping] and rerun autotune. | Coast (Motor Side Inverter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 47 | No Stop Source | No Stop Source The last source for a Stop Command has been removed. Check the configuration and connection of stop commands, such as digital inputs, network connections, and the HIM. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 4 ‘PERIF Flts’ | — | —
Configurable | 48 | Accel Limit | Acceleration Limited The inverter cannot achieve the user-configured acceleration time due to current limiting. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No | 10:1921 [Accel Limit] | —
Configurable | 49 | Decel Limit | Deceleration Limited The inverter cannot achieve the user-configured deceleration time due to limiting imposed by the bus voltage regulator. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No | 10:1922 [Accel Limit] | —
Alarm 1 | 51 | CurLimit Reduced | Current Limit Reduced The current limit value has been reduced from the value set in [Current Limit n] due to excessive IGBT junction temperatures or parameter 10:357 [Drive OL Count] = 95%. See parameter 10:220 [Drive OL Mode]. Possible causes include loads that require too much current and power, improper derating for temperature and altitude, and obstructed airflow. | Verify that the drive is sized and derated correctly. Check the condition of cabinet air filters. | — | — | —
Alarm 2 | 63 | Freq Conflict | Frequency Conflict The values of parameters 10:1898 [Vel Limit Pos] and 10:1899 [Vel Limit Neg] are in conflict with the value of parameter 10:484 [Break Frequency]. | — | — | — | —
Alarm 2 | 64 | VHz Neg Slope | VHz Negative Slope The V/Hz curve segment caused a negative V/Hz slope. | See parameters 10:480 [Start Acc Boost]…10:484 [Break Frequency]. | — | — | —
Alarm 2 | 65 | VHz Boost Limit | VHz Boost Limit Indication that one of the two following conditions exists. Parameters 10:480 [Start Acc Boost] and 10:481 [Run Boost] are greater than parameter 10:400 [Motor NP Volts] x 0.25 when parameter 10:486 [VHz Curve] = 0 ‘Custom V/Hz’. Parameter 10:481 [Run Boost] is greater than parameter 10:400 [Motor NP Volts] x 0.25 when parameter 10:486 [VHz Curve] = 1 ‘Fan/Pump’. | — | — | — | —
Alarm 2 | 70 | Fwd Spd Lim Cfg | Forward Speed Limit Configuration The forward speed reference is out of range. | Verify the settings of 10:425 [PWM Frequency] and 10:1898 [Vel Limit Pos]. Lower carrier frequencies reduce the output frequency range. Verify that 10:1900 [Vel Low Lim Pos] is less than or equal to 10:1898 [Vel Limit Pos]. | — | — | —
Alarm 2 | 71 | Rev Spd Lim Cfg | Reverse Speed Limit Configuration The reverse speed reference is out of range. | Verify the settings of parameters 10:425 [PWM Frequency] and 10:1899 [Vel Limit Neg]. Lower carrier frequencies reduce the output frequency range. Verify that parameter 10:1901 [Vel Low Lim Neg] is greater than or equal to parameter 10:1899 [Vel Limit Neg]. | — | — | —
Alarm 1 | 83 | Fdbk Data Late | Control Feedback data arrived late from SFIB The Control Feedback data arrived to the main control board late from the power layer interface (PLI) board and fiber interface board (FIB). | — | — | — | —
Alarm 1 | 84 | PWM Data Late | PWM data arrived late from ICB The PWM data arrived late from the main control board. | — | — | — | —
Alarm 2 | 89 | Bipolar Conflict | Bipolar Conflict Parameter 10:930 [Direction Mode] is set to 1 “Bipolar” or 2 “Rev Disable” and one or more digital input is enabled for direction control. | — | — | — | —
Resettable Fault | 92 | SW OverCurrent | Software Over Current Motor side inverter current has exceeded the 1 ms current rating. This rating is greater than the current rating for 3 seconds and less than the hardware overcurrent fault level. It is typically 200…250% of the drive continuous rating. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 2 ‘MS Ctrl Flts’ | — | —
Resettable Fault | 93 | HW OverCurrent | Hardware Over Current Output current has exceeded the rating for the product. Possible causes include short circuits in the motor and motor wiring. Perform an insulation resistance test on the wiring to the motor. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 95 | 125us Task Ovr | 125us Task Overrun The 125-microsecond task has overrun the allotted time. | Clear faults. If the fault persists, rerun firmware update. If the fault persists, replace the main control board. | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 96 | 250us Task Ovr | 250us Task Overrun The 250-microsecond task has overrun the allotted time. | Clear faults. If the fault persists, rerun firmware update. If the fault persists, replace the main control board. | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 97 | 1ms Task Ovr | 1ms Task Overrun The 1-millisecond task has overrun the allotted time. | Clear faults. If the fault persists, rerun firmware update. If the fault persists, replace the main control board. | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 98 | 2ms Task Ovr | 2ms Task Overrun The 2-millisecond task has overrun the allotted time. | Clear faults. If the fault persists, rerun firmware update. If the fault persists, replace the main control board. | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 99 | 10ms Task Ovr | 10ms Task Overrun The 10-millisecond task has overrun the allotted time. | Clear faults. If the fault persists, rerun firmware update. If the fault persists, replace the main control board. | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 100 | 100ms Task Ovr | 100ms Task Overrun The 100-millisecond task has overrun the allotted time. | Clear faults. If the fault persists, remove any unnecessary Option Cards from the drive. If the fault persists, re-flash the product. If the fault persists, replace the main control board. | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 101 | CntrlTask Wtchdg | Control Task Watchdog The Control task has failed to complete in the allotted amount of time. | Clear faults. If the fault persists, rerun firmware update. If the fault persists, replace the main control board. | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 102 | SystmTask Wtchdg | System Task Watchdog The System task has failed to complete in the allotted amount of time. | Clear faults. If the fault persists, rerun firmware update. If the fault persists, replace the main control board. | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 103 | 1ms Task Wtchdg | 1ms Task Watchdog The 1-millisecond task has failed to complete in the allotted amount of time. | Clear faults. If the fault persists, rerun firmware update. If the fault persists, replace the main control board. | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 104 | 2ms Task Wtchdg | 2ms Task Watchdog The 2-millisecond task has failed to complete in the allotted amount of time. | Clear faults. If the fault persists, rerun firmware update. If the fault persists, replace the main control board. | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 105 | 10ms Task Wtchdg | 10ms Task Watchdog The 10-millisecond task has failed to complete in the allotted amount of time. | Clear faults. If the fault persists, rerun firmware update. If the fault persists, replace the main control board. | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Configurable | 106 | UnderVoltage | Under Voltage A DC bus undervoltage event has occurred. If the bus voltage in parameter 10:13 [DC Bus Memory] falls below the peak value of the AC line voltage set in parameter 10:286 [UnderVltg Level], then an undervoltage condition exists. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 2 ‘MS Ctrl Flts’ | 10:285 [UnderVltg Action] | —
Resettable Fault | 107 | OverVoltage | Over Voltage DC bus voltage exceeded 120% of the peak value of the rated voltage for the product. Monitor DC bus voltage in parameter 0:3 [DC Bus Volts]. Possible causes include: configuration of line side converter, configuration of DC bus regulator, high inertia loads, and fast decel times. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 110 | Autotune Inertia | Autotune Inertia Out of Range Motor or total inertia determined by the Autotune Inertia Test function is out of range. This condition only occurs during an Inertia Test. | Verify motor nameplate data. Rerun inertia Autotune. | Coast (Motor Side Inverter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Non-Resettable Fault | 111 | Inv App No Strt | Inverter Application Not Start The motor side inverter application failed to start in the DSP. | Cycle power. If the fault persists, rerun firmware update. If the fault persists, replace the main control board. | Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 112 | InvalidLoadRatio | Invalid Load Ratio The total system inertia determined from autotune is less than the value in parameter 10:900 [Motor Inertia], which results in a negative load ratio. This condition is applicable to induction, surface permanent magnet, and interior permanent magnet motors. | Determine if the value of parameter 10:900 [Motor Inertia] is too high. If possible, uncouple the motor from the load and perform the motor inertia autotune test. | Coast (Motor Side Inverter) Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Alarm 2 | 113 | SlipInvalidRange | Invalid Slip Range The motor slip result determined by the Autotune Slip Test function is out of range, or a zero or negative slip is configured for an induction motor. For example, the value of parameter 10:403 [Motor NP RMP] is greater than or equal to parameter 10:404 [Mtr NP Sync Spd]. | Verify motor nameplate data. Ensure parameter 10:403 [Motor NP RPM] is not set to synchronous RPM. Rerun rotate motorID test. | — | — | —
Alarm 2 | 115 | Odd Motor Poles | Odd Number of Motor Poles Configured An odd number of motor poles is configured in parameter 10/11:407 [Motor Poles]. | Change the value of parameter 10/11:407 [Motor Poles] to an even number. | — | — | —
Alarm 2 | 116 | PriVelFbOpen | Primary Velocity Feedback Open The selection for primary velocity feedback is Open Loop, which is not supported for IPM Flux Vector control. | Change the value in parameter 10:1000 [Pri Vel Fb Sel] to select a physical encoder feedback channel. | — | — | —
Alarm 2 | 117 | AltVelFbOpen | Alternate Velocity Feedback Open The selection for alternate velocity feedback is Open Loop, which is not supported for IPM Flux Vector control. | Change the value in parameter 10:1006 [Alt Vel Fb Sel] to select a physical encoder feedback channel. | — | — | —
Event | 129 | Pred Maint Reset | Predictive Maintenance Reset The Predictive Maintenance function has reset an elapsed life parameter. | — | — | —
Event | 130 | MtrSide Started | Motor Side PWM Started The product has started pulse width modulation (PWM) in its motor side power structures. | — | — | — | —
Event | 131 | MtrSide Stopped | Motor Side PWM Stopped The product has stopped pulse width modulation (PWM) in its motor side power structures. | — | — | — | —
Fault Major | 193 | MtrOverVoltage | Motor Over Voltage This condition indicates that the measured motor side voltage feedback 10:11 [Motor Voltage Fb] has exceeded 10:3036 [Mtr Ovr Vlt Trp] for a time duration of 10:3037 [Mtr Ovr Vlt Dly]. | — | Coast Stop Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 2 ‘MS Ctrl Flts’. | — | —
Fault | 197 | IGBT Overcurrent | Power Cell IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Alarm 1 | 198 | IGBT Overcurrent | Power Cell IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Fault | 199 | Cell Overtemp | Power Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Major Fault, as there is no bypass option. For drives with the Bypass option, this fault is also raised if the overtemperature condition in the power cell is detected for a time greater than 10:3019 [CellBypOvrTmpDly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Alarm 1 | 200 | Cell Overtemp | Power Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Fault | 201 | One Phase Loss | Power Cell One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’. | — | —
Alarm 1 | 202 | One Phase Loss | Power Cell One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Fault | 203 | DC OvtVltg Lvl1 | Power Cell LvlOne DC Overvoltage Indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Alarm 1 | 204 | DC OvtVltg Lvl1 | Power Cell Lvl One DC Overvoltage Indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 205 | Cell Bypassed | Power Cell Bypassed This condition indicates that the power cell has been successfully placed in Bypass mode. | — | — | — | —
Fault | 206 | Cell Bypass Fdbk | Power Cell Bypassed Fdbk This condition indicates that, while the drive is running, the Cell Bypass Command to the power cell and the Feedback from the power cell did not match. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 207 | BypassFbkTimeOut | Power Cell Bypassed Fdbk OverTime Indicates that, when the Bypass Command is given to the power cell for the first time, the drive did not receive a valid feedback from the power cell in the time delay specified by 10:3020 [CellByp Fb Delay]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 208 | Cap Vltg Sharing | Power Cell Cap Voltage Sharing This condition indicates that the voltage of the middle capacitor is 40V higher or lower than one third of DC bus voltage. | — | Coast Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’. | — | —
Fault | 209 | DC Bus Under Vltg | Power Cell DC Bus Under Voltage This condition indicates that the power cell DC voltage is lower than 370V DC with tolerance of ±15V DC. The value can be adjusted by 12:4 [DCBusUndVltg Trp]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’. | — | —
Fault | 210 | Cell Bypass HW | Power Cell Bypass Hardware Fault This condition indicates that the bypass command has been received by the power cell, but the bypass circuit is not functional. | — | Coast Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 211 | Two Phase Loss | Power Cell Two Phase Loss This condition indicates that two or more AC phases at the power cell input have been lost. | — | Coast Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 212 | DC OvrVltg Lvl2 | Power Cell Lvl Two DC Overvoltage Indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 2. The trip levels and time delay are specified by 12:7 [DCBusOvrVltg2Trp] and 12:8 [DCBusOvrVltg2Dly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 213 | Fiber Comm Loss | Power Cell Communication Loss This condition indicates a loss of fiber communication between XCVR board and the power cell. This is raised when the Main Control starts modulation but does not receive a gating acknowledge from the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 214 | Fmw Compatibility | Power Cell Firmware Incompatibile This condition indicates that the power cell firmware is not compatible with the power cell hardware. | — | Coast Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 215 | No PWM Pulse | Power Cell No PWM Pulse This condition indicates that the power cell did not receive PWM pulses from the Main Controller. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault Major | 216 | Drv Overcurrent | Drive Overcurrent Indicates that the measured drive/motor current has exceeded the instantaneous capability of the power cell. For Frame A drives it is 135% and for Frame B drives it is 165% of the Power Cell Current Rating, shown in parameter 12:32 [U0 Rated Amps] or 12:52 [V0 Rated Amps]. | — | Coast Stop Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 217 | Mtr Neut OvrVltg | Motor Neutral Overvoltage Indicates that the calculated Motor Neutral Voltage indicated by 10:3035 [Neutral Vlt Fb] has exceeded the trip setting 10:3033 [NeutralOvrVltTrp] for a time delay specified in 10:3034 [NeutralOvrVltDly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’. | — | —
Resettable Fault | 218 | Mtr OverCurrent | Motor Overcurrent Indicates that the measured motor side current has exceeded 250% of the 10/11:401 [Motor NP Amps] for a time delay of 10 ms. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’. | — | —
Alarm 2 | 219 | CellByp Disabled | Cell Bypass Disabled This condition indicates the Cell Bypass feature has been disabled due to one or more power cells do not have Bypass Hardware Installed. | To run the drive set parameter 10:3016 [CellBypassEnable] to 0 'Disable'. | — | — | —
Alarm 1 | 220 | Output Freq Lmt | Output Frequency Limit This condition indicates that the velocity command is greater than product capability. Consult the factory. | — | — | — | —
Alarm 1 | 221 | Power Loss Dtctd | Power Loss Detected The drive detected that the DC bus has reached parameter 10:272 [Pwr Loss A Level] or 10:276 [Pwr Loss B Level] and initiated an action determined by parameter 10:271 [Pwr Loss Mode A] or 10:275 [Pwr Loss Mode B]. | — | — | — | —

## Port 12
Condition Type | Condition Code | Display Text | Fault | Action | Fault Action | Configuration Parameter | Configurable Action
none | 0 | No Entry
Event | 90 | PCU0RunTimeChngd | Power Cell U0 Run Time Changed This event indicates that the user changed the Run Time value for the specified power cell. | — | — | — | —
Event | 91 | PCU1RunTimeChngd | Power Cell U1 Run Time Changed This event indicates that the user changed the Run Time value for the specified power cell. | — | — | — | —
Event | 92 | PCU2RunTimeChngd | Power Cell U2 Run Time Changed This event indicates that the user changed the Run Time value for the specified power cell. | — | — | — | —
Event | 93 | PCU3RunTimeChngd | Power Cell U3 Run Time Changed This event indicates that the user changed the Run Time value for the specified power cell. | — | — | — | —
Event | 94 | PCU4RunTimeChngd | Power Cell U4 Run Time Changed This event indicates that the user changed the Run Time value for the specified power cell. | — | — | — | —
Event | 95 | PCU5RunTimeChngd | Power Cell U5 Run Time Changed This event indicates that the user changed the Run Time value for the specified power cell. | — | — | — | —
Event | 96 | PCU6RunTimeChngd | Power Cell U6 Run Time Changed This event indicates that the user changed the Run Time value for the specified power cell. | — | — | — | —
Event | 97 | PCU7RunTimeChngd | Power Cell U7 Run Time Changed This event indicates that the user changed the Run Time value for the specified power cell. | — | — | — | —
Event | 98 | PCU8RunTimeChngd | Power Cell U8 Run Time Changed This event indicates that the user changed the Run Time value for the specified power cell. | — | — | — | —
Event | 100 | PCV0RunTimeChngd | Power Cell V0 Run Time Changed This event indicates that the user changed the Run Time value for the specified power cell. | — | — | — | —
Event | 101 | PCV1RunTimeChngd | Power Cell V1 Run Time Changed This event indicates that the user changed the Run Time value for the specified power cell. | — | — | — | —
Event | 102 | PCV2RunTimeChngd | Power Cell V2 Run Time Changed This event indicates that the user changed the Run Time value for the specified power cell. | — | — | — | —
Event | 103 | PCV3RunTimeChngd | Power Cell V3 Run Time Changed This event indicates that the user changed the Run Time value for the specified power cell. | — | — | — | —
Event | 104 | PCV4RunTimeChngd | Power Cell V4 Run Time Changed This event indicates that the user changed the Run Time value for the specified power cell. | — | — | — | —
Event | 105 | PCV5RunTimeChngd | Power Cell V5 Run Time Changed This event indicates that the user changed the Run Time value for the specified power cell. | — | — | — | —
Event | 106 | PCV6RunTimeChngd | Power Cell V6 Run Time Changed This event indicates that the user changed the Run Time value for the specified power cell. | — | — | — | —
Event | 107 | PCV7RunTimeChngd | Power Cell V7 Run Time Changed This event indicates that the user changed the Run Time value for the specified power cell. | — | — | — | —
Event | 108 | PCV8RunTimeChngd | Power Cell V8 Run Time Changed This event indicates that the user changed the Run Time value for the specified power cell. | — | — | — | —
Event | 110 | PCW0RunTimeChngd | Power Cell W0 Run Time Changed This event indicates that the user changed the Run Time value for the specified power cell. | — | — | — | —
Event | 111 | PCW1RunTimeChngd | Power Cell W1 Run Time Changed This event indicates that the user changed the Run Time value for the specified power cell. | — | — | — | —
Event | 112 | PCW2RunTimeChngd | Power Cell W2 Run Time Changed This event indicates that the user changed the Run Time value for the specified power cell. | — | — | — | —
Event | 113 | PCW3RunTimeChngd | Power Cell W3 Run Time Changed This event indicates that the user changed the Run Time value for the specified power cell. | — | — | — | —
Event | 114 | PCW4RunTimeChngd | Power Cell W4 Run Time Changed This event indicates that the user changed the Run Time value for the specified power cell. | — | — | — | —
Event | 115 | PCW5RunTimeChngd | Power Cell W5 Run Time Changed This event indicates that the user changed the Run Time value for the specified power cell. | — | — | — | —
Event | 116 | PCW6RunTimeChngd | Power Cell W6 Run Time Changed This event indicates that the user changed the Run Time value for the specified power cell. | — | — | — | —
Event | 117 | PCW7RunTimeChngd | Power Cell W7 Run Time Changed This event indicates that the user changed the Run Time value for the specified power cell. | — | — | — | —
Event | 118 | PCW8RunTimeChngd | Power Cell W8 Run Time Changed This event indicates that the user changed the Run Time value for the specified power cell. | — | — | — | —
Alarm 1 | 120 | Rplc PC U0- 90d | Replace Power Cell U0 in 90 days This condition indicates that the specified power cell needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 121 | Rplc PC U1- 90d | Replace Power Cell U1 in 90 days This condition indicates that the specified power cell needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 122 | Rplc PC U2- 90d | Replace Power Cell U2 in 90 days This condition indicates that the specified power cell needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 123 | Rplc PC U3- 90d | Replace Power Cell U3 in 90 days This condition indicates that the specified power cell needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 124 | Rplc PC U4- 90d | Replace Power Cell U4 in 90 days This condition indicates that the specified power cell needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 125 | Rplc PC U5- 90d | Replace Power Cell U5 in 90 days This condition indicates that the specified power cell needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 126 | Rplc PC U6- 90d | Replace Power Cell U6 in 90 days This condition indicates that the specified power cell needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 127 | Rplc PC U7- 90d | Replace Power Cell U7 in 90 days This condition indicates that the specified power cell needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 128 | Rplc PC U8- 90d | Replace Power Cell U8 in 90 days This condition indicates that the specified power cell needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 130 | Rplc PC V0- 90d | Replace Power Cell V0 in 90 days This condition indicates that the specified power cell needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 131 | Rplc PC V1- 90d | Replace Power Cell V1 in 90 days This condition indicates that the specified power cell needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 132 | Rplc PC V2- 90d | Replace Power Cell V2 in 90 days This condition indicates that the specified power cell needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 133 | Rplc PC V3- 90d | Replace Power Cell V3 in 90 days This condition indicates that the specified power cell needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 134 | Rplc PC V4- 90d | Replace Power Cell V4 in 90 days This condition indicates that the specified power cell needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 135 | Rplc PC V5- 90d | Replace Power Cell V5 in 90 days This condition indicates that the specified power cell needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 136 | Rplc PC V6- 90d | Replace Power Cell V6 in 90 days This condition indicates that the specified power cell needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 137 | Rplc PC V7- 90d | Replace Power Cell V7 in 90 days This condition indicates that the specified power cell needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 138 | Rplc PC V8- 90d | Replace Power Cell V8 in 90 days This condition indicates that the specified power cell needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 140 | Rplc PC W0- 90d | Replace Power Cell W0 in 90 days This condition indicates that the specified power cell needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 141 | Rplc PC W1- 90d | Replace Power Cell W1 in 90 days This condition indicates that the specified power cell needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 142 | Rplc PC W2- 90d | Replace Power Cell W2 in 90 days This condition indicates that the specified power cell needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 143 | Rplc PC W3- 90d | Replace Power Cell W3 in 90 days This condition indicates that the specified power cell needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 144 | Rplc PC W4- 90d | Replace Power Cell W4 in 90 days This condition indicates that the specified power cell needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 145 | Rplc PC W5- 90d | Replace Power Cell W5 in 90 days This condition indicates that the specified power cell needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 146 | Rplc PC W6- 90d | Replace Power Cell W6 in 90 days This condition indicates that the specified power cell needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 147 | Rplc PC W7- 90d | Replace Power Cell W7 in 90 days This condition indicates that the specified power cell needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 148 | Rplc PC W8- 90d | Replace Power Cell W8 in 90 days This condition indicates that the specified power cell needs to be replaced within 90 days. | — | — | — | —
Fault | 150 | U0IGBTOvercurrent | U0 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 151 | U1IGBTOvercurrent | U1 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 152 | U2IGBTOvercurrent | U2 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 153 | U3IGBTOvercurrent | U3 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 154 | U4IGBTOvercurrent | U4 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 155 | U5IGBTOvercurrent | U5 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 156 | U6IGBTOvercurrent | U6 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 157 | U7IGBTOvercurrent | U7 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 158 | U8IGBTOvercurrent | U8 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Alarm 1 | 160 | U0IGBTOvercurrent | U0 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 161 | U1IGBTOvercurrent | U1 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 162 | U2IGBTOvercurrent | U2 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 163 | U3IGBTOvercurrent | U3 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 164 | U4IGBTOvercurrent | U4 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 165 | U5IGBTOvercurrent | U5 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 166 | U6IGBTOvercurrent | U6 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 167 | U7IGBTOvercurrent | U7 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 168 | U8IGBTOvercurrent | U8 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Fault | 170 | V0IGBTOvercurrent | V0 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 171 | V1IGBTOvercurrent | V1 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 172 | V2IGBTOvercurrent | V2 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 173 | V3IGBTOvercurrent | V3 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 174 | V4IGBTOvercurrent | V4 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 175 | V5IGBTOvercurrent | V5 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 176 | V6IGBTOvercurrent | V6 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 177 | V7IGBTOvercurrent | V7 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 178 | V8IGBTOvercurrent | V8 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Alarm 1 | 180 | V0IGBTOvercurrent | V0 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 181 | V1IGBTOvercurrent | V1 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 182 | V2IGBTOvercurrent | V2 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 183 | V3IGBTOvercurrent | V3 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 184 | V4IGBTOvercurrent | V4 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 185 | V5IGBTOvercurrent | V5 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 186 | V6IGBTOvercurrent | V6 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 187 | V7IGBTOvercurrent | V7 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 188 | V8IGBTOvercurrent | V8 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Fault | 190 | W0IGBTOvercurrent | W0 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 191 | W1IGBTOvercurrent | W1 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 192 | W2IGBTOvercurrent | W2 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 193 | W3IGBTOvercurrent | W3 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 194 | W4IGBTOvercurrent | W4 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 195 | W5IGBTOvercurrent | W5 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 196 | W6IGBTOvercurrent | W6 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 197 | W7IGBTOvercurrent | W7 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 198 | W8IGBTOvercurrent | W8 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Alarm 1 | 200 | W0IGBTOvercurrent | W0 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 201 | W1IGBTOvercurrent | W1 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 202 | W2IGBTOvercurrent | W2 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 203 | W3IGBTOvercurrent | W3 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 204 | W4IGBTOvercurrent | W4 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 205 | W5IGBTOvercurrent | W5 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 206 | W6IGBTOvercurrent | W6 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 207 | W7IGBTOvercurrent | W7 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 208 | W8IGBTOvercurrent | W8 IGBT Overcurrent This condition indicates either there is a problem with the specific IGBT gate drive board or there is an IGBT short circuit. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Fault | 210 | U0 Cell Overtemp | U0 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Major Fault, as there is no bypass option. For drives with the bypass option, this fault is also raised if the overtemperature condition in the power cell is detected for a time greater than in 10:3019 [CellBypOvrTmpDly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 211 | U1 Cell Overtemp | U1 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Major Fault, as there is no bypass option. For drives with the bypass option, this fault is also raised if the overtemperature condition in the power cell is detected for a time greater than in 10:3019 [CellBypOvrTmpDly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 212 | U2 Cell Overtemp | U2 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Major Fault, as there is no bypass option. For drives with the bypass option, this fault is also raised if the overtemperature condition in the power cell is detected for a time greater than in 10:3019 [CellBypOvrTmpDly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 213 | U3 Cell Overtemp | U3 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Major Fault, as there is no bypass option. For drives with the bypass option, this fault is also raised if the overtemperature condition in the power cell is detected for a time greater than in 10:3019 [CellBypOvrTmpDly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 214 | U4 Cell Overtemp | U4 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Major Fault, as there is no bypass option. For drives with the bypass option, this fault is also raised if the overtemperature condition in the power cell is detected for a time greater than in 10:3019 [CellBypOvrTmpDly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 215 | U5 Cell Overtemp | U5 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Major Fault, as there is no bypass option. For drives with the bypass option, this fault is also raised if the overtemperature condition in the power cell is detected for a time greater than in 10:3019 [CellBypOvrTmpDly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 216 | U6 Cell Overtemp | U6 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Major Fault, as there is no bypass option. For drives with the bypass option, this fault is also raised if the overtemperature condition in the power cell is detected for a time greater than in 10:3019 [CellBypOvrTmpDly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 217 | U7 Cell Overtemp | U7 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Major Fault, as there is no bypass option. For drives with the bypass option, this fault is also raised if the overtemperature condition in the power cell is detected for a time greater than in 10:3019 [CellBypOvrTmpDly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 218 | U8 Cell Overtemp | U8 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Major Fault, as there is no bypass option. For drives with the bypass option, this fault is also raised if the overtemperature condition in the power cell is detected for a time greater than in 10:3019 [CellBypOvrTmpDly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Alarm 1 | 220 | U0 Cell Overtemp | U0 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 221 | U1 Cell Overtemp | U1 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 222 | U2 Cell Overtemp | U2 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 223 | U3 Cell Overtemp | U3 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 224 | U4 Cell Overtemp | U4 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 225 | U5 Cell Overtemp | U5 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 226 | U6 Cell Overtemp | U6 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 227 | U7 Cell Overtemp | U7 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 228 | U8 Cell Overtemp | U8 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Fault | 230 | Port 12 V0 Cell Overtemp | V0 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Major Fault, as there is no bypass option. For drives with the bypass option, this fault is also raised if the overtemperature condition in the power cell is detected for a time greater than in 10:3019 [CellBypOvrTmpDly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 231 | V1 Cell Overtemp | V1 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Major Fault, as there is no bypass option. For drives with the bypass option, this fault is also raised if the overtemperature condition in the power cell is detected for a time greater than in 10:3019 [CellBypOvrTmpDly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 232 | V2 Cell Overtemp | V2 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Major Fault, as there is no bypass option. For drives with the bypass option, this fault is also raised if the overtemperature condition in the power cell is detected for a time greater than in 10:3019 [CellBypOvrTmpDly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 233 | V3 Cell Overtemp | V3 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Major Fault, as there is no bypass option. For drives with the bypass option, this fault is also raised if the overtemperature condition in the power cell is detected for a time greater than in 10:3019 [CellBypOvrTmpDly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 234 | V4 Cell Overtemp | V4 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Major Fault, as there is no bypass option. For drives with the bypass option, this fault is also raised if the overtemperature condition in the power cell is detected for a time greater than in 10:3019 [CellBypOvrTmpDly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 235 | V5 Cell Overtemp | V5 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Major Fault, as there is no bypass option. For drives with the bypass option, this fault is also raised if the overtemperature condition in the power cell is detected for a time greater than in 10:3019 [CellBypOvrTmpDly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 236 | V6 Cell Overtemp | V6 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Major Fault, as there is no bypass option. For drives with the bypass option, this fault is also raised if the overtemperature condition in the power cell is detected for a time greater than in 10:3019 [CellBypOvrTmpDly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 237 | V7 Cell Overtemp | V7 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Major Fault, as there is no bypass option. For drives with the bypass option, this fault is also raised if the overtemperature condition in the power cell is detected for a time greater than in 10:3019 [CellBypOvrTmpDly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 238 | V8 Cell Overtemp | V8 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Major Fault, as there is no bypass option. For drives with the bypass option, this fault is also raised if the overtemperature condition in the power cell is detected for a time greater than in 10:3019 [CellBypOvrTmpDly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Alarm 1 | 240 | V0 Cell Overtemp | V0 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 241 | V1 Cell Overtemp | V1 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 242 | V2 Cell Overtemp | V2 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 243 | V3 Cell Overtemp | V3 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 244 | V4 Cell Overtemp | V4 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 245 | V5 Cell Overtemp | V5 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 246 | V6 Cell Overtemp | V6 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 247 | V7 Cell Overtemp | V7 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 248 | V8 Cell Overtemp | V8 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Fault | 250 | W0 Cell Overtemp | W0 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Major Fault, as there is no bypass option. For drives with the bypass option, this fault is also raised if the overtemperature condition in the power cell is detected for a time greater than in 10:3019 [CellBypOvrTmpDly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 251 | W1 Cell Overtemp | W1 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Major Fault, as there is no bypass option. For drives with the bypass option, this fault is also raised if the overtemperature condition in the power cell is detected for a time greater than in 10:3019 [CellBypOvrTmpDly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 252 | W2 Cell Overtemp | W2 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Major Fault, as there is no bypass option. For drives with the bypass option, this fault is also raised if the overtemperature condition in the power cell is detected for a time greater than in 10:3019 [CellBypOvrTmpDly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 253 | W3 Cell Overtemp | W3 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Major Fault, as there is no bypass option. For drives with the bypass option, this fault is also raised if the overtemperature condition in the power cell is detected for a time greater than in 10:3019 [CellBypOvrTmpDly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 254 | W4 Cell Overtemp | W4 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Major Fault, as there is no bypass option. For drives with the bypass option, this fault is also raised if the overtemperature condition in the power cell is detected for a time greater than in 10:3019 [CellBypOvrTmpDly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 255 | W5 Cell Overtemp | W5 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Major Fault, as there is no bypass option. For drives with the bypass option, this fault is also raised if the overtemperature condition in the power cell is detected for a time greater than in 10:3019 [CellBypOvrTmpDly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 256 | W6 Cell Overtemp | W6 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Major Fault, as there is no bypass option. For drives with the bypass option, this fault is also raised if the overtemperature condition in the power cell is detected for a time greater than in 10:3019 [CellBypOvrTmpDly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 257 | W7 Cell Overtemp | W7 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Major Fault, as there is no bypass option. For drives with the bypass option, this fault is also raised if the overtemperature condition in the power cell is detected for a time greater than in 10:3019 [CellBypOvrTmpDly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 258 | W8 Cell Overtemp | W8 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Major Fault, as there is no bypass option. For drives with the bypass option, this fault is also raised if the overtemperature condition in the power cell is detected for a time greater than in 10:3019 [CellBypOvrTmpDly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Alarm 1 | 260 | W0 Cell Overtemp | W0 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 261 | W1 Cell Overtemp | W1 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 262 | W2 Cell Overtemp | W2 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 263 | W3 Cell Overtemp | W3 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 264 | W4 Cell Overtemp | W4 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 265 | W5 Cell Overtemp | W5 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 266 | W6 Cell Overtemp | W6 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 267 | W7 Cell Overtemp | W7 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 268 | W8 Cell Overtemp | W8 Cell Overtemperature This condition indicates an overtemperature on the heat sink used for cooling power cell IGBTs. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Fault | 270 | U0 OnePhaseLoss | U0 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 271 | U1 OnePhaseLoss | U1 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 272 | U2 OnePhaseLoss | U2 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 273 | U3 OnePhaseLoss | U3 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 274 | U4 OnePhaseLoss | U4 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 275 | U5 OnePhaseLoss | U5 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 276 | U6 OnePhaseLoss | U6 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 277 | U7 OnePhaseLoss | U7 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 278 | U8 OnePhaseLoss | U8 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Alarm 1 | 280 | U0 OnePhaseLoss | U0 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 281 | U1 OnePhaseLoss | U1 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 282 | U2 OnePhaseLoss | U2 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 283 | U3 OnePhaseLoss | U3 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 284 | U4 OnePhaseLoss | U4 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 285 | U5 OnePhaseLoss | U5 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 286 | U6 OnePhaseLoss | U6 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 287 | U7 OnePhaseLoss | U7 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 288 | U8 OnePhaseLoss | U8 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Fault | 290 | V0 OnePhaseLoss | V0 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 291 | V1 OnePhaseLoss | V1 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 292 | V2 OnePhaseLoss | V2 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 293 | V3 OnePhaseLoss | V3 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 294 | V4 OnePhaseLoss | V4 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 295 | V5 OnePhaseLoss | V5 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 296 | V6 OnePhaseLoss | V6 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 297 | V7 OnePhaseLoss | V7 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 298 | V8 OnePhaseLoss | V8 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Alarm 1 | 300 | V0 OnePhaseLoss | V0 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 301 | V1 OnePhaseLoss | V1 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 302 | V2 OnePhaseLoss | V2 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 303 | V3 OnePhaseLoss | V3 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 304 | V4 OnePhaseLoss | V4 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 305 | V5 OnePhaseLoss | V5 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 306 | V6 OnePhaseLoss | V6 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 307 | V7 OnePhaseLoss | V7 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 308 | V8 OnePhaseLoss | V8 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Fault | 310 | W0 OnePhaseLoss | W0 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 311 | W1 OnePhaseLoss | W1 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 312 | W2 OnePhaseLoss | W2 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 313 | W3 OnePhaseLoss | W3 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 314 | W4 OnePhaseLoss | W4 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 315 | W5 OnePhaseLoss | W5 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 316 | W6 OnePhaseLoss | W6 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 317 | W7 OnePhaseLoss | W7 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 318 | W8 OnePhaseLoss | W8 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Alarm 1 | 320 | W0 OnePhaseLoss | W0 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 321 | W1 OnePhaseLoss | W1 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 322 | W2 OnePhaseLoss | W2 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 323 | W3 OnePhaseLoss | W3 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 324 | W4 OnePhaseLoss | W4 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 325 | W5 OnePhaseLoss | W5 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 326 | W6 OnePhaseLoss | W6 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 327 | W7 OnePhaseLoss | W7 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 328 | W8 OnePhaseLoss | W8 One Phase Loss This condition indicates that one AC phase at the power cell input has been lost. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Fault | 330 | U0 DCOvrVltgLvl1 | U0 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 331 | U1 DCOvrVltgLvl1 | U1 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 332 | U2 DCOvrVltgLvl1 | U2 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 333 | U3 DCOvrVltgLvl1 | U3 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 334 | U4 DCOvrVltgLvl1 | U4 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 335 | U5 DCOvrVltgLvl1 | U5 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 336 | U6 DCOvrVltgLvl1 | U6 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 337 | U7 DCOvrVltgLvl1 | U7 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 338 | U8 DCOvrVltgLvl1 | U8 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Alarm 1 | 340 | U0 DCOvrVltgLvl1 | U0 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 341 | U1 DCOvrVltgLvl1 | U1 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 342 | U2 DCOvrVltgLvl1 | U2 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 343 | U3 DCOvrVltgLvl1 | U3 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 344 | U4 DCOvrVltgLvl1 | U4 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 345 | U5 DCOvrVltgLvl1 | U5 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 346 | U6 DCOvrVltgLvl1 | U6 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 347 | U7 DCOvrVltgLvl1 | U7 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 348 | U8 DCOvrVltgLvl1 | U8 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Fault | 350 | V0 DCOvrVltgLvl1 | V0 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 351 | V1 DCOvrVltgLvl1 | V1 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 352 | V2 DCOvrVltgLvl1 | V2 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 353 | V3 DCOvrVltgLvl1 | V3 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 354 | V4 DCOvrVltgLvl1 | V4 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 355 | V5 DCOvrVltgLvl1 | V5 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 356 | V6 DCOvrVltgLvl1 | V6 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 357 | V7 DCOvrVltgLvl1 | V7 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 358 | V8 DCOvrVltgLvl1 | V8 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Alarm 1 | 360 | V0 DCOvrVltgLvl1 | V0 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 361 | V1 DCOvrVltgLvl1 | V1 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 362 | V2 DCOvrVltgLvl1 | V2 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 363 | V3 DCOvrVltgLvl1 | V3 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 364 | V4 DCOvrVltgLvl1 | V4 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 365 | V5 DCOvrVltgLvl1 | V5 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 366 | V6 DCOvrVltgLvl1 | V6 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 367 | V7 DCOvrVltgLvl1 | V7 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 368 | V8 DCOvrVltgLvl1 | V8 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Fault | 370 | W0 DCOvrVltgLvl1 | W0 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 371 | W1 DCOvrVltgLvl1 | W1 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 372 | W2 DCOvrVltgLvl1 | W2 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 373 | W3 DCOvrVltgLvl1 | W3 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 374 | W4 DCOvrVltgLvl1 | W4 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 375 | W5 DCOvrVltgLvl1 | W5 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 376 | W6 DCOvrVltgLvl1 | W6 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 377 | W7 DCOvrVltgLvl1 | W7 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 378 | W8 DCOvrVltgLvl1 | W8 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Major Fault, as there is no bypass option. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Alarm 1 | 380 | W0 DCOvrVltgLvl1 | W0 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 381 | W1 DCOvrVltgLvl1 | W1 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 382 | W2 DCOvrVltgLvl1 | W2 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 383 | W3 DCOvrVltgLvl1 | W3 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 384 | W4 DCOvrVltgLvl1 | W4 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 385 | W5 DCOvrVltgLvl1 | W5 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 386 | W6 DCOvrVltgLvl1 | W6 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 387 | W7 DCOvrVltgLvl1 | W7 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 388 | W8 DCOvrVltgLvl1 | W8 DC Overvoltage Level 1 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 1. The trip levels and time delay are specified by 12:5 [DCBusOvrVltg1Trp] and 12:6 [DCBusOvrVltg1Dly]. The drive raises a Type 1 alarm since the power cell can be operated in bypass mode. | — | — | — | —
Alarm 1 | 390 | U0 Cell Bypassed | U0 Cell Bypassed This condition indicates that the power cell has been successfully placed in Bypass mode. | — | — | — | —
Alarm 1 | 391 | U1 Cell Bypassed | U1 Cell Bypassed This condition indicates that the power cell has been successfully placed in Bypass mode. | — | — | — | —
Alarm 1 | 392 | U2 Cell Bypassed | U2 Cell Bypassed This condition indicates that the power cell has been successfully placed in Bypass mode. | — | — | — | —
Alarm 1 | 393 | U3 Cell Bypassed | U3 Cell Bypassed This condition indicates that the power cell has been successfully placed in Bypass mode. | — | — | — | —
Alarm 1 | 394 | U4 Cell Bypassed | U4 Cell Bypassed This condition indicates that the power cell has been successfully placed in Bypass mode. | — | — | — | —
Alarm 1 | 395 | U5 Cell Bypassed | U5 Cell Bypassed This condition indicates that the power cell has been successfully placed in Bypass mode. | — | — | — | —
Alarm 1 | 396 | U6 Cell Bypassed | U6 Cell Bypassed This condition indicates that the power cell has been successfully placed in Bypass mode. | — | — | — | —
Alarm 1 | 397 | U7 Cell Bypassed | U7 Cell Bypassed This condition indicates that the power cell has been successfully placed in Bypass mode. | — | — | — | —
Alarm 1 | 398 | U8 Cell Bypassed | U8 Cell Bypassed This condition indicates that the power cell has been successfully placed in Bypass mode. | — | — | — | —
Alarm 1 | 400 | V0 Cell Bypassed | V0 Cell Bypassed This condition indicates that the power cell has been successfully placed in Bypass mode. | — | — | — | —
Alarm 1 | 401 | V1 Cell Bypassed | V1 Cell Bypassed This condition indicates that the power cell has been successfully placed in Bypass mode. | — | — | — | —
Alarm 1 | 402 | V2 Cell Bypassed | V2 Cell Bypassed This condition indicates that the power cell has been successfully placed in Bypass mode. | — | — | — | —
Alarm 1 | 403 | V3 Cell Bypassed | V3 Cell Bypassed This condition indicates that the power cell has been successfully placed in Bypass mode. | — | — | — | —
Alarm 1 | 404 | V4 Cell Bypassed | V4 Cell Bypassed This condition indicates that the power cell has been successfully placed in Bypass mode. | — | — | — | —
Alarm 1 | 405 | V5 Cell Bypassed | V5 Cell Bypassed This condition indicates that the power cell has been successfully placed in Bypass mode. | — | — | — | —
Alarm 1 | 406 | V6 Cell Bypassed | V6 Cell Bypassed This condition indicates that the power cell has been successfully placed in Bypass mode. | — | — | — | —
Alarm 1 | 407 | V7 Cell Bypassed | V7 Cell Bypassed This condition indicates that the power cell has been successfully placed in Bypass mode. | — | — | — | —
Alarm 1 | 408 | V8 Cell Bypassed | V8 Cell Bypassed This condition indicates that the power cell has been successfully placed in Bypass mode. | — | — | — | —
Fault | 410 | W0 Cell Bypassed | W0 Cell Bypassed This condition indicates that the power cell has been successfully placed in Bypass mode. | — | — | — | —
Fault | 411 | W1 Cell Bypassed | W1 Cell Bypassed This condition indicates that the power cell has been successfully placed in Bypass mode. | — | — | — | —
Fault | 412 | W2 Cell Bypassed | W2 Cell Bypassed This condition indicates that the power cell has been successfully placed in Bypass mode. | — | — | — | —
Fault | 413 | W3 Cell Bypassed | W3 Cell Bypassed This condition indicates that the power cell has been successfully placed in Bypass mode. | — | — | — | —
Fault | 414 | W4 Cell Bypassed | W4 Cell Bypassed This condition indicates that the power cell has been successfully placed in Bypass mode. | — | — | — | —
Fault | 415 | W5 Cell Bypassed | W5 Cell Bypassed This condition indicates that the power cell has been successfully placed in Bypass mode. | — | — | — | —
Fault | 416 | W6 Cell Bypassed | W6 Cell Bypassed This condition indicates that the power cell has been successfully placed in Bypass mode. | — | — | — | —
Fault | 417 | W7 Cell Bypassed | W7 Cell Bypassed This condition indicates that the power cell has been successfully placed in Bypass mode. | — | — | — | —
Fault | 418 | W8 Cell Bypassed | W8 Cell Bypassed This condition indicates that the power cell has been successfully placed in Bypass mode. | — | — | — | —
Fault | 420 | U0CellBypassFdbk | U0 Cell Bypass Feedback This condition indicates that Cell Bypass Command and Feedback did not match. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 421 | U1CellBypassFdbk | U1 Cell Bypass Feedback This condition indicates that Cell Bypass Command and Feedback did not match. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 422 | U2CellBypassFdbk | U2 Cell Bypass Feedback This condition indicates that Cell Bypass Command and Feedback did not match. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 423 | U3CellBypassFdbk | U3 Cell Bypass Feedback This condition indicates that Cell Bypass Command and Feedback did not match. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 424 | U4CellBypassFdbk | U4 Cell Bypass Feedback This condition indicates that Cell Bypass Command and Feedback did not match. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 425 | U5CellBypassFdbk | U5 Cell Bypass Feedback This condition indicates that Cell Bypass Command and Feedback did not match. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 426 | U6CellBypassFdbk | U6 Cell Bypass Feedback This condition indicates that Cell Bypass Command and Feedback did not match. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 427 | U7CellBypassFdbk | U7 Cell Bypass Feedback This condition indicates that Cell Bypass Command and Feedback did not match. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 428 | U8CellBypassFdbk | U8 Cell Bypass Feedback This condition indicates that Cell Bypass Command and Feedback did not match. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 430 | V0CellBypassFdbk | V0 Cell Bypass Feedback This condition indicates that Cell Bypass Command and Feedback did not match. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 431 | V1CellBypassFdbk | V1 Cell Bypass Feedback This condition indicates that Cell Bypass Command and Feedback did not match. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 432 | V2CellBypassFdbk | V2 Cell Bypass Feedback This condition indicates that Cell Bypass Command and Feedback did not match. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 433 | V3CellBypassFdbk | V3 Cell Bypass Feedback This condition indicates that Cell Bypass Command and Feedback did not match. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 434 | V4CellBypassFdbk | V4 Cell Bypass Feedback This condition indicates that Cell Bypass Command and Feedback did not match. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 435 | V5CellBypassFdbk | V5 Cell Bypass Feedback This condition indicates that Cell Bypass Command and Feedback did not match. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 436 | V6CellBypassFdbk | V6 Cell Bypass Feedback This condition indicates that Cell Bypass Command and Feedback did not match. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 437 | V7CellBypassFdbk | V7 Cell Bypass Feedback This condition indicates that Cell Bypass Command and Feedback did not match. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 438 | V8CellBypassFdbk | V8 Cell Bypass Feedback This condition indicates that Cell Bypass Command and Feedback did not match. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 440 | W0CellBypassFdbk | W0 Cell Bypass Feedback This condition indicates that Cell Bypass Command and Feedback did not match. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 441 | W1CellBypassFdbk | W1 Cell Bypass Feedback This condition indicates that Cell Bypass Command and Feedback did not match. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 442 | W2CellBypassFdbk | W2 Cell Bypass Feedback This condition indicates that Cell Bypass Command and Feedback did not match. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 443 | W3CellBypassFdbk | W3 Cell Bypass Feedback This condition indicates that Cell Bypass Command and Feedback did not match. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 444 | W4CellBypassFdbk | W4 Cell Bypass Feedback This condition indicates that Cell Bypass Command and Feedback did not match. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 445 | W5CellBypassFdbk | W5 Cell Bypass Feedback This condition indicates that Cell Bypass Command and Feedback did not match. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 446 | W6CellBypassFdbk | W6 Cell Bypass Feedback This condition indicates that Cell Bypass Command and Feedback did not match. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 447 | W7CellBypassFdbk | W7 Cell Bypass Feedback This condition indicates that Cell Bypass Command and Feedback did not match. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 448 | W8CellBypassFdbk | W8 Cell Bypass Feedback This condition indicates that Cell Bypass Command and Feedback did not match. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 450 | U0 BypFbkTimeOut | U0 Bypass Feedback Time Out This condition indicates that when the Power Cell Bypass Command was given, the drive did not get a valid feedback from the power cell in the time delay specified by 10:3020 [CellByp Fb Delay]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 451 | U1 BypFbkTimeOut | U1 Bypass Feedback Time Out This condition indicates that when the Power Cell Bypass Command was given, the drive did not get a valid feedback from the power cell in the time delay specified by 10:3020 [CellByp Fb Delay]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 452 | U2 BypFbkTimeOut | U2 Bypass Feedback Time Out This condition indicates that when the Power Cell Bypass Command was given, the drive did not get a valid feedback from the power cell in the time delay specified by 10:3020 [CellByp Fb Delay]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 453 | U3 BypFbkTimeOut | U3 Bypass Feedback Time Out This condition indicates that when the Power Cell Bypass Command was given, the drive did not get a valid feedback from the power cell in the time delay specified by 10:3020 [CellByp Fb Delay]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 454 | U4 BypFbkTimeOut | U4 Bypass Feedback Time Out This condition indicates that when the Power Cell Bypass Command was given, the drive did not get a valid feedback from the power cell in the time delay specified by 10:3020 [CellByp Fb Delay]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 455 | U5 BypFbkTimeOut | U5 Bypass Feedback Time Out This condition indicates that when the Power Cell Bypass Command was given, the drive did not get a valid feedback from the power cell in the time delay specified by 10:3020 [CellByp Fb Delay]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 456 | U6 BypFbkTimeOut | U6 Bypass Feedback Time Out This condition indicates that when the Power Cell Bypass Command was given, the drive did not get a valid feedback from the power cell in the time delay specified by 10:3020 [CellByp Fb Delay]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 457 | U7 BypFbkTimeOut | U7 Bypass Feedback Time Out This condition indicates that when the Power Cell Bypass Command was given, the drive did not get a valid feedback from the power cell in the time delay specified by 10:3020 [CellByp Fb Delay]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 458 | U8 BypFbkTimeOut | U8 Bypass Feedback Time Out This condition indicates that when the Power Cell Bypass Command was given, the drive did not get a valid feedback from the power cell in the time delay specified by 10:3020 [CellByp Fb Delay]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 460 | V0 BypFbkTimeOut | V0 Bypass Feedback Time Out This condition indicates that when the Power Cell Bypass Command was given, the drive did not get a valid feedback from the power cell in the time delay specified by 10:3020 [CellByp Fb Delay]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 461 | V1 BypFbkTimeOut | V1 Bypass Feedback Time Out This condition indicates that when the Power Cell Bypass Command was given, the drive did not get a valid feedback from the power cell in the time delay specified by 10:3020 [CellByp Fb Delay]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 462 | V2 BypFbkTimeOut | V2 Bypass Feedback Time Out This condition indicates that when the Power Cell Bypass Command was given, the drive did not get a valid feedback from the power cell in the time delay specified by 10:3020 [CellByp Fb Delay]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 463 | V3 BypFbkTimeOut | V3 Bypass Feedback Time Out This condition indicates that when the Power Cell Bypass Command was given, the drive did not get a valid feedback from the power cell in the time delay specified by 10:3020 [CellByp Fb Delay]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 464 | V4 BypFbkTimeOut | V4 Bypass Feedback Time Out This condition indicates that when the Power Cell Bypass Command was given, the drive did not get a valid feedback from the power cell in the time delay specified by 10:3020 [CellByp Fb Delay]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 465 | V5 BypFbkTimeOut | V5 Bypass Feedback Time Out This condition indicates that when the Power Cell Bypass Command was given, the drive did not get a valid feedback from the power cell in the time delay specified by 10:3020 [CellByp Fb Delay]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 466 | V6 BypFbkTimeOut | V6 Bypass Feedback Time Out This condition indicates that when the Power Cell Bypass Command was given, the drive did not get a valid feedback from the power cell in the time delay specified by 10:3020 [CellByp Fb Delay]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 467 | V7 BypFbkTimeOut | V7 Bypass Feedback Time Out This condition indicates that when the Power Cell Bypass Command was given, the drive did not get a valid feedback from the power cell in the time delay specified by 10:3020 [CellByp Fb Delay]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 468 | V8 BypFbkTimeOut | V8 Bypass Feedback Time Out This condition indicates that when the Power Cell Bypass Command was given, the drive did not get a valid feedback from the power cell in the time delay specified by 10:3020 [CellByp Fb Delay]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 470 | W0 BypFbkTimeOut | W0 Bypass Feedback Time Out This condition indicates that when the Power Cell Bypass Command was given, the drive did not get a valid feedback from the power cell in the time delay specified by 10:3020 [CellByp Fb Delay]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 471 | W1 BypFbkTimeOut | W1 Bypass Feedback Time Out This condition indicates that when the Power Cell Bypass Command was given, the drive did not get a valid feedback from the power cell in the time delay specified by 10:3020 [CellByp Fb Delay]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 472 | W2 BypFbkTimeOut | W2 Bypass Feedback Time Out This condition indicates that when the Power Cell Bypass Command was given, the drive did not get a valid feedback from the power cell in the time delay specified by 10:3020 [CellByp Fb Delay]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 473 | W3 BypFbkTimeOut | W3 Bypass Feedback Time Out This condition indicates that when the Power Cell Bypass Command was given, the drive did not get a valid feedback from the power cell in the time delay specified by 10:3020 [CellByp Fb Delay]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 474 | W4 BypFbkTimeOut | W4 Bypass Feedback Time Out This condition indicates that when the Power Cell Bypass Command was given, the drive did not get a valid feedback from the power cell in the time delay specified by 10:3020 [CellByp Fb Delay]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 475 | W5 BypFbkTimeOut | W5 Bypass Feedback Time Out This condition indicates that when the Power Cell Bypass Command was given, the drive did not get a valid feedback from the power cell in the time delay specified by 10:3020 [CellByp Fb Delay]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 476 | W6 BypFbkTimeOut | W6 Bypass Feedback Time Out This condition indicates that when the Power Cell Bypass Command was given, the drive did not get a valid feedback from the power cell in the time delay specified by 10:3020 [CellByp Fb Delay]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 477 | W7 BypFbkTimeOut | W7 Bypass Feedback Time Out This condition indicates that when the Power Cell Bypass Command was given, the drive did not get a valid feedback from the power cell in the time delay specified by 10:3020 [CellByp Fb Delay]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 478 | W8 BypFbkTimeOut | W8 Bypass Feedback Time Out This condition indicates that when the Power Cell Bypass Command was given, the drive did not get a valid feedback from the power cell in the time delay specified by 10:3020 [CellByp Fb Delay]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 480 | U0CapVltgSharing | U0 Capacitor Voltage Sharing This condition indicates that the voltage of the middle capacitor is 40V higher or lower than one third of DC bus voltage. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 481 | U1CapVltgSharing | U1 Capacitor Voltage Sharing This condition indicates that the voltage of the middle capacitor is 40V higher or lower than one third of DC bus voltage. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 482 | U2CapVltgSharing | U2 Capacitor Voltage Sharing This condition indicates that the voltage of the middle capacitor is 40V higher or lower than one third of DC bus voltage. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 483 | U3CapVltgSharing | U3 Capacitor Voltage Sharing This condition indicates that the voltage of the middle capacitor is 40V higher or lower than one third of DC bus voltage. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 484 | U4CapVltgSharing | U4 Capacitor Voltage Sharing This condition indicates that the voltage of the middle capacitor is 40V higher or lower than one third of DC bus voltage. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 485 | U5CapVltgSharing | U5 Capacitor Voltage Sharing This condition indicates that the voltage of the middle capacitor is 40V higher or lower than one third of DC bus voltage. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 486 | U6CapVltgSharing | U6 Capacitor Voltage Sharing This condition indicates that the voltage of the middle capacitor is 40V higher or lower than one third of DC bus voltage. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 487 | U7CapVltgSharing | U7 Capacitor Voltage Sharing This condition indicates that the voltage of the middle capacitor is 40V higher or lower than one third of DC bus voltage. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 488 | U8CapVltgSharing | U8 Capacitor Voltage Sharing This condition indicates that the voltage of the middle capacitor is 40V higher or lower than one third of DC bus voltage. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 490 | V0CapVltgSharing | V0 Capacitor Voltage Sharing This condition indicates that the voltage of the middle capacitor is 40V higher or lower than one third of DC bus voltage. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 491 | V1CapVltgSharing | V1 Capacitor Voltage Sharing This condition indicates that the voltage of the middle capacitor is 40V higher or lower than one third of DC bus voltage. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 492 | V2CapVltgSharing | V2 Capacitor Voltage Sharing This condition indicates that the voltage of the middle capacitor is 40V higher or lower than one third of DC bus voltage. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 493 | V3CapVltgSharing | V3 Capacitor Voltage Sharing This condition indicates that the voltage of the middle capacitor is 40V higher or lower than one third of DC bus voltage. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 494 | V4CapVltgSharing | V4 Capacitor Voltage Sharing This condition indicates that the voltage of the middle capacitor is 40V higher or lower than one third of DC bus voltage. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 495 | V5CapVltgSharing | V5 Capacitor Voltage Sharing This condition indicates that the voltage of the middle capacitor is 40V higher or lower than one third of DC bus voltage. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 496 | V6CapVltgSharing | V6 Capacitor Voltage Sharing This condition indicates that the voltage of the middle capacitor is 40V higher or lower than one third of DC bus voltage. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 497 | V7CapVltgSharing | V7 Capacitor Voltage Sharing This condition indicates that the voltage of the middle capacitor is 40V higher or lower than one third of DC bus voltage. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 498 | V8CapVltgSharing | V8 Capacitor Voltage Sharing This condition indicates that the voltage of the middle capacitor is 40V higher or lower than one third of DC bus voltage. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 500 | W0CapVltgSharing | W0 Capacitor Voltage Sharing This condition indicates that the voltage of the middle capacitor is 40V higher or lower than one third of DC bus voltage. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 501 | W1CapVltgSharing | W1 Capacitor Voltage Sharing This condition indicates that the voltage of the middle capacitor is 40V higher or lower than one third of DC bus voltage. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 502 | W2CapVltgSharing | W2 Capacitor Voltage Sharing This condition indicates that the voltage of the middle capacitor is 40V higher or lower than one third of DC bus voltage. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 503 | W3CapVltgSharing | W3 Capacitor Voltage Sharing This condition indicates that the voltage of the middle capacitor is 40V higher or lower than one third of DC bus voltage. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 504 | W4CapVltgSharing | W4 Capacitor Voltage Sharing This condition indicates that the voltage of the middle capacitor is 40V higher or lower than one third of DC bus voltage. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 505 | W5CapVltgSharing | W5 Capacitor Voltage Sharing This condition indicates that the voltage of the middle capacitor is 40V higher or lower than one third of DC bus voltage. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 506 | W6CapVltgSharing | W6 Capacitor Voltage Sharing This condition indicates that the voltage of the middle capacitor is 40V higher or lower than one third of DC bus voltage. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 507 | W7CapVltgSharing | W7 Capacitor Voltage Sharing This condition indicates that the voltage of the middle capacitor is 40V higher or lower than one third of DC bus voltage. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 508 | W8CapVltgSharing | W8 Capacitor Voltage Sharing This condition indicates that the voltage of the middle capacitor is 40V higher or lower than one third of DC bus voltage. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 510 | U0DCBusUnderVltg | U0 DC Bus Undervoltage This condition indicates that the power cell DC voltage is lower than 370Vdc with tolerance of ±15V DC. The value can be adjusted by 12:4 [DCBusUndVltg Trp]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 511 | U1DCBusUnderVltg | U1 DC Bus Undervoltage This condition indicates that the power cell DC voltage is lower than 370Vdc with tolerance of ±15V DC. The value can be adjusted by 12:4 [DCBusUndVltg Trp]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 512 | U2DCBusUnderVltg | U2 DC Bus Undervoltage This condition indicates that the power cell DC voltage is lower than 370Vdc with tolerance of ±15V DC. The value can be adjusted by 12:4 [DCBusUndVltg Trp]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 513 | U3DCBusUnderVltg | U3 DC Bus Undervoltage This condition indicates that the power cell DC voltage is lower than 370Vdc with tolerance of ±15V DC. The value can be adjusted by 12:4 [DCBusUndVltg Trp]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 514 | U4DCBusUnderVltg | U4 DC Bus Undervoltage This condition indicates that the power cell DC voltage is lower than 370Vdc with tolerance of ±15V DC. The value can be adjusted by 12:4 [DCBusUndVltg Trp]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 515 | U5DCBusUnderVltg | U5 DC Bus Undervoltage This condition indicates that the power cell DC voltage is lower than 370Vdc with tolerance of ±15V DC. The value can be adjusted by 12:4 [DCBusUndVltg Trp]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 516 | U6DCBusUnderVltg | U6 DC Bus Undervoltage This condition indicates that the power cell DC voltage is lower than 370Vdc with tolerance of ±15V DC. The value can be adjusted by 12:4 [DCBusUndVltg Trp]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 517 | U7DCBusUnderVltg | U7 DC Bus Undervoltage This condition indicates that the power cell DC voltage is lower than 370Vdc with tolerance of ±15V DC. The value can be adjusted by 12:4 [DCBusUndVltg Trp]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 518 | U8DCBusUnderVltg | U8 DC Bus Undervoltage This condition indicates that the power cell DC voltage is lower than 370Vdc with tolerance of ±15V DC. The value can be adjusted by 12:4 [DCBusUndVltg Trp]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 520 | V0DCBusUnderVltg | V0 DC Bus Undervoltage This condition indicates that the power cell DC voltage is lower than 370Vdc with tolerance of ±15V DC. The value can be adjusted by 12:4 [DCBusUndVltg Trp]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 521 | V1DCBusUnderVltg | V1 DC Bus Undervoltage This condition indicates that the power cell DC voltage is lower than 370Vdc with tolerance of ±15V DC. The value can be adjusted by 12:4 [DCBusUndVltg Trp]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 522 | V2DCBusUnderVltg | V2 DC Bus Undervoltage This condition indicates that the power cell DC voltage is lower than 370Vdc with tolerance of ±15V DC. The value can be adjusted by 12:4 [DCBusUndVltg Trp]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 523 | V3DCBusUnderVltg | V3 DC Bus Undervoltage This condition indicates that the power cell DC voltage is lower than 370Vdc with tolerance of ±15V DC. The value can be adjusted by 12:4 [DCBusUndVltg Trp]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 524 | V4DCBusUnderVltg | V4 DC Bus Undervoltage This condition indicates that the power cell DC voltage is lower than 370Vdc with tolerance of ±15V DC. The value can be adjusted by 12:4 [DCBusUndVltg Trp]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 525 | V5DCBusUnderVltg | V5 DC Bus Undervoltage This condition indicates that the power cell DC voltage is lower than 370Vdc with tolerance of ±15V DC. The value can be adjusted by 12:4 [DCBusUndVltg Trp]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 526 | V6DCBusUnderVltg | V6 DC Bus Undervoltage This condition indicates that the power cell DC voltage is lower than 370Vdc with tolerance of ±15V DC. The value can be adjusted by 12:4 [DCBusUndVltg Trp]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 527 | V7DCBusUnderVltg | V7 DC Bus Undervoltage This condition indicates that the power cell DC voltage is lower than 370Vdc with tolerance of ±15V DC. The value can be adjusted by 12:4 [DCBusUndVltg Trp]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 528 | V8DCBusUnderVltg | V8 DC Bus Undervoltage This condition indicates that the power cell DC voltage is lower than 370Vdc with tolerance of ±15V DC. The value can be adjusted by 12:4 [DCBusUndVltg Trp]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 530 | W0DCBusUnderVltg | W0 DC Bus Undervoltage This condition indicates that the power cell DC voltage is lower than 370Vdc with tolerance of ±15V DC. The value can be adjusted by 12:4 [DCBusUndVltg Trp]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 531 | W1DCBusUnderVltg | W1 DC Bus Undervoltage This condition indicates that the power cell DC voltage is lower than 370Vdc with tolerance of ±15V DC. The value can be adjusted by 12:4 [DCBusUndVltg Trp]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 532 | W2DCBusUnderVltg | W2 DC Bus Undervoltage This condition indicates that the power cell DC voltage is lower than 370Vdc with tolerance of ±15V DC. The value can be adjusted by 12:4 [DCBusUndVltg Trp]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 533 | W3DCBusUnderVltg | V3 DC Bus Undervoltage This condition indicates that the power cell DC voltage is lower than 370Vdc with tolerance of ±15V DC. The value can be adjusted by 12:4 [DCBusUndVltg Trp]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 534 | W4DCBusUnderVltg | W4 DC Bus Undervoltage This condition indicates that the power cell DC voltage is lower than 370Vdc with tolerance of ±15V DC. The value can be adjusted by 12:4 [DCBusUndVltg Trp]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 535 | W5DCBusUnderVltg | W5 DC Bus Undervoltage This condition indicates that the power cell DC voltage is lower than 370Vdc with tolerance of ±15V DC. The value can be adjusted by 12:4 [DCBusUndVltg Trp]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 536 | W6DCBusUnderVltg | W6 DC Bus Undervoltage This condition indicates that the power cell DC voltage is lower than 370Vdc with tolerance of ±15V DC. The value can be adjusted by 12:4 [DCBusUndVltg Trp]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 537 | W7DCBusUnderVltg | W7 DC Bus Undervoltage This condition indicates that the power cell DC voltage is lower than 370Vdc with tolerance of ±15V DC. The value can be adjusted by 12:4 [DCBusUndVltg Trp]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 538 | W8DCBusUnderVltg | W8 DC Bus Undervoltage This condition indicates that the power cell DC voltage is lower than 370Vdc with tolerance of ±15V DC. The value can be adjusted by 12:4 [DCBusUndVltg Trp]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 540 | U0 No PWM Pulse | U0 No PWM Pulse For IGBT This condition indicates that the power cell did not receive PWM pulses from the main controller. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 541 | U1 No PWM Pulse | U1 No PWM Pulse For IGBT This condition indicates that the power cell did not receive PWM pulses from the main controller. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 542 | U2 No PWM Pulse | U2 No PWM Pulse For IGBT This condition indicates that the power cell did not receive PWM pulses from the main controller. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 543 | U3 No PWM Pulse | U3 No PWM Pulse For IGBT This condition indicates that the power cell did not receive PWM pulses from the main controller. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 544 | U4 No PWM Pulse | U4 No PWM Pulse For IGBT This condition indicates that the power cell did not receive PWM pulses from the main controller. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 545 | U5 No PWM Pulse | U5 No PWM Pulse For IGBT This condition indicates that the power cell did not receive PWM pulses from the main controller. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 546 | U6 No PWM Pulse | U6 No PWM Pulse For IGBT This condition indicates that the power cell did not receive PWM pulses from the main controller. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 547 | U7 No PWM Pulse | U7 No PWM Pulse For IGBT This condition indicates that the power cell did not receive PWM pulses from the main controller. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 548 | U8 No PWM Pulse | U8 No PWM Pulse For IGBT This condition indicates that the power cell did not receive PWM pulses from the main controller. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 550 | V0 No PWM Pulse | V0 No PWM Pulse For IGBT This condition indicates that the power cell did not receive PWM pulses from the main controller. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 551 | V1 No PWM Pulse | V1 No PWM Pulse For IGBT This condition indicates that the power cell did not receive PWM pulses from the main controller. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 552 | V2 No PWM Pulse | V2 No PWM Pulse For IGBT This condition indicates that the power cell did not receive PWM pulses from the main controller. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 553 | V3 No PWM Pulse | V3 No PWM Pulse For IGBT This condition indicates that the power cell did not receive PWM pulses from the main controller. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 554 | V4 No PWM Pulse | V4 No PWM Pulse For IGBT This condition indicates that the power cell did not receive PWM pulses from the main controller. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 555 | V5 No PWM Pulse | V5 No PWM Pulse For IGBT This condition indicates that the power cell did not receive PWM pulses from the main controller. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 556 | V6 No PWM Pulse | V6 No PWM Pulse For IGBT This condition indicates that the power cell did not receive PWM pulses from the main controller. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 557 | V7 No PWM Pulse | V7 No PWM Pulse For IGBT This condition indicates that the power cell did not receive PWM pulses from the main controller. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 558 | V8 No PWM Pulse | V8 No PWM Pulse For IGBT This condition indicates that the power cell did not receive PWM pulses from the main controller. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 560 | W0 No PWM Pulse | W0 No PWM Pulse For IGBT This condition indicates that the power cell did not receive PWM pulses from the main controller. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 561 | W1 No PWM Pulse | W1 No PWM Pulse For IGBT This condition indicates that the power cell did not receive PWM pulses from the main controller. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 562 | W2 No PWM Pulse | W2 No PWM Pulse For IGBT This condition indicates that the power cell did not receive PWM pulses from the main controller. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 563 | W3 No PWM Pulse | W3 No PWM Pulse For IGBT This condition indicates that the power cell did not receive PWM pulses from the main controller. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 564 | W4 No PWM Pulse | W4 No PWM Pulse For IGBT This condition indicates that the power cell did not receive PWM pulses from the main controller. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 565 | W5 No PWM Pulse | W5 No PWM Pulse For IGBT This condition indicates that the power cell did not receive PWM pulses from the main controller. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 566 | W6 No PWM Pulse | W6 No PWM Pulse For IGBT This condition indicates that the power cell did not receive PWM pulses from the main controller. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 567 | W7 No PWM Pulse | W7 No PWM Pulse For IGBT This condition indicates that the power cell did not receive PWM pulses from the main controller. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 568 | W8 No PWM Pulse | W8 No PWM Pulse For IGBT This condition indicates that the power cell did not receive PWM pulses from the main controller. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 570 | U0Cell Bypass HW | U0 Cell Bypass Hardware Fault This condition indicates that the bypass command has been received by the power cell, but the bypass circuit is not functional. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 571 | U1Cell Bypass HW | U1 Cell Bypass Hardware Fault This condition indicates that the bypass command has been received by the power cell, but the bypass circuit is not functional. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 572 | U2Cell Bypass HW | U2 Cell Bypass Hardware Fault This condition indicates that the bypass command has been received by the power cell, but the bypass circuit is not functional. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 573 | U3Cell Bypass HW | U3 Cell Bypass Hardware Fault This condition indicates that the bypass command has been received by the power cell, but the bypass circuit is not functional. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 574 | U4Cell Bypass HW | U4 Cell Bypass Hardware Fault This condition indicates that the bypass command has been received by the power cell, but the bypass circuit is not functional. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 575 | U5Cell Bypass HW | U5 Cell Bypass Hardware Fault This condition indicates that the bypass command has been received by the power cell, but the bypass circuit is not functional. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 576 | U6Cell Bypass HW | U6 Cell Bypass Hardware Fault This condition indicates that the bypass command has been received by the power cell, but the bypass circuit is not functional. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 577 | U7Cell Bypass HW | U7 Cell Bypass Hardware Fault This condition indicates that the bypass command has been received by the power cell, but the bypass circuit is not functional. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 578 | U8Cell Bypass HW | U8 Cell Bypass Hardware Fault This condition indicates that the bypass command has been received by the power cell, but the bypass circuit is not functional. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 580 | V0Cell Bypass HW | V0 Cell Bypass Hardware Fault This condition indicates that the bypass command has been received by the power cell, but the bypass circuit is not functional. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 581 | V1Cell Bypass HW | V1 Cell Bypass Hardware Fault This condition indicates that the bypass command has been received by the power cell, but the bypass circuit is not functional. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 582 | V2Cell Bypass HW | V2 Cell Bypass Hardware Fault This condition indicates that the bypass command has been received by the power cell, but the bypass circuit is not functional. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 583 | V3Cell Bypass HW | V3 Cell Bypass Hardware Fault This condition indicates that the bypass command has been received by the power cell, but the bypass circuit is not functional. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 584 | V4Cell Bypass HW | V4 Cell Bypass Hardware Fault This condition indicates that the bypass command has been received by the power cell, but the bypass circuit is not functional. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 585 | V5Cell Bypass HW | V5 Cell Bypass Hardware Fault This condition indicates that the bypass command has been received by the power cell, but the bypass circuit is not functional. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 586 | V6Cell Bypass HW | V6 Cell Bypass Hardware Fault This condition indicates that the bypass command has been received by the power cell, but the bypass circuit is not functional. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 587 | V7Cell Bypass HW | V7 Cell Bypass Hardware Fault This condition indicates that the bypass command has been received by the power cell, but the bypass circuit is not functional. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 588 | V8Cell Bypass HW | V8 Cell Bypass Hardware Fault This condition indicates that the bypass command has been received by the power cell, but the bypass circuit is not functional. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 590 | W0Cell Bypass HW | W0 Cell Bypass Hardware Fault This condition indicates that the bypass command has been received by the power cell, but the bypass circuit is not functional. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 591 | W1Cell Bypass HW | W1 Cell Bypass Hardware Fault This condition indicates that the bypass command has been received by the power cell, but the bypass circuit is not functional. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 592 | W2Cell Bypass HW | W2 Cell Bypass Hardware Fault This condition indicates that the bypass command has been received by the power cell, but the bypass circuit is not functional. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 593 | W3Cell Bypass HW | W3 Cell Bypass Hardware Fault This condition indicates that the bypass command has been received by the power cell, but the bypass circuit is not functional. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 594 | W4Cell Bypass HW | W4 Cell Bypass Hardware Fault This condition indicates that the bypass command has been received by the power cell, but the bypass circuit is not functional. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 595 | W5Cell Bypass HW | W5 Cell Bypass Hardware Fault This condition indicates that the bypass command has been received by the power cell, but the bypass circuit is not functional. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 596 | W6Cell Bypass HW | W6 Cell Bypass Hardware Fault This condition indicates that the bypass command has been received by the power cell, but the bypass circuit is not functional. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 597 | W7Cell Bypass HW | W7 Cell Bypass Hardware Fault This condition indicates that the bypass command has been received by the power cell, but the bypass circuit is not functional. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 598 | W8Cell Bypass HW | W8 Cell Bypass Hardware Fault This condition indicates that the bypass command has been received by the power cell, but the bypass circuit is not functional. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 600 | U0Two Phase Loss | U0 Two Phase Loss This condition indicates that two or more AC phases at the power cell input have been lost. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 601 | U1Two Phase Loss | U1 Two Phase Loss This condition indicates that two or more AC phases at the power cell input have been lost. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 602 | U2Two Phase Loss | U2 Two Phase Loss This condition indicates that two or more AC phases at the power cell input have been lost. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 603 | U3Two Phase Loss | U3 Two Phase Loss This condition indicates that two or more AC phases at the power cell input have been lost. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 604 | U4Two Phase Loss | U4 Two Phase Loss This condition indicates that two or more AC phases at the power cell input have been lost. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 605 | U5Two Phase Loss | U5 Two Phase Loss This condition indicates that two or more AC phases at the power cell input have been lost. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 606 | U6Two Phase Loss | U6 Two Phase Loss This condition indicates that two or more AC phases at the power cell input have been lost. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 607 | U7Two Phase Loss | U7 Two Phase Loss This condition indicates that two or more AC phases at the power cell input have been lost. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 608 | U8Two Phase Loss | U8 Two Phase Loss This condition indicates that two or more AC phases at the power cell input have been lost. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 610 | V0Two Phase Loss | V0 Two Phase Loss This condition indicates that two or more AC phases at the power cell input have been lost. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 611 | V1Two Phase Loss | V1 Two Phase Loss This condition indicates that two or more AC phases at the power cell input have been lost. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 612 | V2Two Phase Loss | V2 Two Phase Loss This condition indicates that two or more AC phases at the power cell input have been lost. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 613 | V3Two Phase Loss | V3 Two Phase Loss This condition indicates that two or more AC phases at the power cell input have been lost. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 614 | V4Two Phase Loss | V4 Two Phase Loss This condition indicates that two or more AC phases at the power cell input have been lost. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 615 | V5Two Phase Loss | V5 Two Phase Loss This condition indicates that two or more AC phases at the power cell input have been lost. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 616 | V6Two Phase Loss | V6 Two Phase Loss This condition indicates that two or more AC phases at the power cell input have been lost. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 617 | V7Two Phase Loss | V7 Two Phase Loss This condition indicates that two or more AC phases at the power cell input have been lost. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 618 | V8Two Phase Loss | V8 Two Phase Loss This condition indicates that two or more AC phases at the power cell input have been lost. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 620 | W0Two Phase Loss | W0 Two Phase Loss This condition indicates that two or more AC phases at the power cell input have been lost. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 621 | W1Two Phase Loss | W1 Two Phase Loss This condition indicates that two or more AC phases at the power cell input have been lost. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 622 | W2Two Phase Loss | W2 Two Phase Loss This condition indicates that two or more AC phases at the power cell input have been lost. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 623 | W3Two Phase Loss | W3 Two Phase Loss This condition indicates that two or more AC phases at the power cell input have been lost. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 624 | W4Two Phase Loss | W4 Two Phase Loss This condition indicates that two or more AC phases at the power cell input have been lost. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 625 | W5Two Phase Loss | W5 Two Phase Loss This condition indicates that two or more AC phases at the power cell input have been lost. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 626 | W6Two Phase Loss | W6 Two Phase Loss This condition indicates that two or more AC phases at the power cell input have been lost. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 627 | W7Two Phase Loss | W7 Two Phase Loss This condition indicates that two or more AC phases at the power cell input have been lost. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 628 | W8Two Phase Loss | W8 Two Phase Loss This condition indicates that two or more AC phases at the power cell input have been lost. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 630 | U0 DCOvrVltgLvl2 | U0 DC Overvoltage Level 2 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 2. The trip levels and time delay are specified by 12:7 [DCBusOvrVltg2Trp] and 12:8 [DCBusOvrVltg2Dly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 631 | U1 DCOvrVltgLvl2 | U1 DC Overvoltage Level 2 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 2. The trip levels and time delay are specified by 12:7 [DCBusOvrVltg2Trp] and 12:8 [DCBusOvrVltg2Dly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 632 | U2 DCOvrVltgLvl2 | U2 DC Overvoltage Level 2 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 2. The trip levels and time delay are specified by 12:7 [DCBusOvrVltg2Trp] and 12:8 [DCBusOvrVltg2Dly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 633 | U3 DCOvrVltgLvl2 | U3 DC Overvoltage Level 2 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 2. The trip levels and time delay are specified by 12:7 [DCBusOvrVltg2Trp] and 12:8 [DCBusOvrVltg2Dly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 634 | U4 DCOvrVltgLvl2 | U4 DC Overvoltage Level 2 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 2. The trip levels and time delay are specified by 12:7 [DCBusOvrVltg2Trp] and 12:8 [DCBusOvrVltg2Dly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 635 | U5 DCOvrVltgLvl2 | U5 DC Overvoltage Level 2 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 2. The trip levels and time delay are specified by 12:7 [DCBusOvrVltg2Trp] and 12:8 [DCBusOvrVltg2Dly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 636 | U6 DCOvrVltgLvl2 | U6 DC Overvoltage Level 2 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 2. The trip levels and time delay are specified by 12:7 [DCBusOvrVltg2Trp] and 12:8 [DCBusOvrVltg2Dly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 637 | U7 DCOvrVltgLvl2 | U7 DC Overvoltage Level 2 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 2. The trip levels and time delay are specified by 12:7 [DCBusOvrVltg2Trp] and 12:8 [DCBusOvrVltg2Dly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 638 | U8 DCOvrVltgLvl2 | U8 DC Overvoltage Level 2 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 2. The trip levels and time delay are specified by 12:7 [DCBusOvrVltg2Trp] and 12:8 [DCBusOvrVltg2Dly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 640 | V0 DCOvrVltgLvl2 | V0 DC Overvoltage Level 2 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 2. The trip levels and time delay are specified by 12:7 [DCBusOvrVltg2Trp] and 12:8 [DCBusOvrVltg2Dly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 641 | V1 DCOvrVltgLvl2 | V1 DC Overvoltage Level 2 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 2. The trip levels and time delay are specified by 12:7 [DCBusOvrVltg2Trp] and 12:8 [DCBusOvrVltg2Dly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 642 | V2 DCOvrVltgLvl2 | V2 DC Overvoltage Level 2 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 2. The trip levels and time delay are specified by 12:7 [DCBusOvrVltg2Trp] and 12:8 [DCBusOvrVltg2Dly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 643 | V3 DCOvrVltgLvl2 | V3 DC Overvoltage Level 2 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 2. The trip levels and time delay are specified by 12:7 [DCBusOvrVltg2Trp] and 12:8 [DCBusOvrVltg2Dly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 644 | V4 DCOvrVltgLvl2 | V4 DC Overvoltage Level 2 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 2. The trip levels and time delay are specified by 12:7 [DCBusOvrVltg2Trp] and 12:8 [DCBusOvrVltg2Dly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 645 | V5 DCOvrVltgLvl2 | V5 DC Overvoltage Level 2 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 2. The trip levels and time delay are specified by 12:7 [DCBusOvrVltg2Trp] and 12:8 [DCBusOvrVltg2Dly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 646 | V6 DCOvrVltgLvl2 | V6 DC Overvoltage Level 2 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 2. The trip levels and time delay are specified by 12:7 [DCBusOvrVltg2Trp] and 12:8 [DCBusOvrVltg2Dly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 647 | V7 DCOvrVltgLvl2 | V7 DC Overvoltage Level 2 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 2. The trip levels and time delay are specified by 12:7 [DCBusOvrVltg2Trp] and 12:8 [DCBusOvrVltg2Dly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 648 | V8 DCOvrVltgLvl2 | V8 DC Overvoltage Level 2 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 2. The trip levels and time delay are specified by 12:7 [DCBusOvrVltg2Trp] and 12:8 [DCBusOvrVltg2Dly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 650 | W0 DCOvrVltgLvl2 | W0 DC Overvoltage Level 2 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 2. The trip levels and time delay are specified by 12:7 [DCBusOvrVltg2Trp] and 12:8 [DCBusOvrVltg2Dly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 651 | W1 DCOvrVltgLvl2 | W1 DC Overvoltage Level 2 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 2. The trip levels and time delay are specified by 12:7 [DCBusOvrVltg2Trp] and 12:8 [DCBusOvrVltg2Dly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 652 | W2 DCOvrVltgLvl2 | W2 DC Overvoltage Level 2 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 2. The trip levels and time delay are specified by 12:7 [DCBusOvrVltg2Trp] and 12:8 [DCBusOvrVltg2Dly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 653 | W3 DCOvrVltgLvl2 | W3 DC Overvoltage Level 2 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 2. The trip levels and time delay are specified by 12:7 [DCBusOvrVltg2Trp] and 12:8 [DCBusOvrVltg2Dly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 654 | W4 DCOvrVltgLvl2 | W4 DC Overvoltage Level 2 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 2. The trip levels and time delay are specified by 12:7 [DCBusOvrVltg2Trp] and 12:8 [DCBusOvrVltg2Dly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 655 | W5 DCOvrVltgLvl2 | W5 DC Overvoltage Level 2 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 2. The trip levels and time delay are specified by 12:7 [DCBusOvrVltg2Trp] and 12:8 [DCBusOvrVltg2Dly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 656 | W6 DCOvrVltgLvl2 | W6 DC Overvoltage Level 2 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 2. The trip levels and time delay are specified by 12:7 [DCBusOvrVltg2Trp] and 12:8 [DCBusOvrVltg2Dly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 657 | W7 DCOvrVltgLvl2 | W7 DC Overvoltage Level 2 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 2. The trip levels and time delay are specified by 12:7 [DCBusOvrVltg2Trp] and 12:8 [DCBusOvrVltg2Dly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 658 | W8 DCOvrVltgLvl2 | W8 DC Overvoltage Level 2 This condition indicates that the power cell DC bus peak voltage detected by the hardware has reached Level 2. The trip levels and time delay are specified by 12:7 [DCBusOvrVltg2Trp] and 12:8 [DCBusOvrVltg2Dly]. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 660 | U0 FiberCommLoss | U0 Fiber Communication Loss This condition indicates a loss of fiber communication between the XCVR board and the power cell. This is raised when the Main Control starts modulation but does not receive a gating acknowledge from the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 661 | U1 FiberCommLoss | U1 Fiber Communication Loss This condition indicates a loss of fiber communication between the XCVR board and the power cell. This is raised when the Main Control starts modulation but does not receive a gating acknowledge from the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 662 | U2 FiberCommLoss | U2 Fiber Communication Loss This condition indicates a loss of fiber communication between the XCVR board and the power cell. This is raised when the Main Control starts modulation but does not receive a gating acknowledge from the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 663 | U3 FiberCommLoss | U3 Fiber Communication Loss This condition indicates a loss of fiber communication between the XCVR board and the power cell. This is raised when the Main Control starts modulation but does not receive a gating acknowledge from the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 664 | U4 FiberCommLoss | U4 Fiber Communication Loss This condition indicates a loss of fiber communication between the XCVR board and the power cell. This is raised when the Main Control starts modulation but does not receive a gating acknowledge from the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 665 | U5 FiberCommLoss | U5 Fiber Communication Loss This condition indicates a loss of fiber communication between the XCVR board and the power cell. This is raised when the Main Control starts modulation but does not receive a gating acknowledge from the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 666 | U6 FiberCommLoss | U6 Fiber Communication Loss This condition indicates a loss of fiber communication between the XCVR board and the power cell. This is raised when the Main Control starts modulation but does not receive a gating acknowledge from the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 667 | U7 FiberCommLoss | U7 Fiber Communication Loss This condition indicates a loss of fiber communication between the XCVR board and the power cell. This is raised when the Main Control starts modulation but does not receive a gating acknowledge from the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 668 | U8 FiberCommLoss | U8 Fiber Communication Loss This condition indicates a loss of fiber communication between the XCVR board and the power cell. This is raised when the Main Control starts modulation but does not receive a gating acknowledge from the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 670 | V0 FiberCommLoss | V0 Fiber Communication Loss This condition indicates a loss of fiber communication between the XCVR board and the power cell. This is raised when the Main Control starts modulation but does not receive a gating acknowledge from the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 671 | V1 FiberCommLoss | V1 Fiber Communication Loss This condition indicates a loss of fiber communication between the XCVR board and the power cell. This is raised when the Main Control starts modulation but does not receive a gating acknowledge from the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 672 | V2 FiberCommLoss | V2 Fiber Communication Loss This condition indicates a loss of fiber communication between the XCVR board and the power cell. This is raised when the Main Control starts modulation but does not receive a gating acknowledge from the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 673 | V3 FiberCommLoss | V3 Fiber Communication Loss This condition indicates a loss of fiber communication between the XCVR board and the power cell. This is raised when the Main Control starts modulation but does not receive a gating acknowledge from the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 674 | V4 FiberCommLoss | V4 Fiber Communication Loss This condition indicates a loss of fiber communication between the XCVR board and the power cell. This is raised when the Main Control starts modulation but does not receive a gating acknowledge from the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 675 | V5 FiberCommLoss | V5 Fiber Communication Loss This condition indicates a loss of fiber communication between the XCVR board and the power cell. This is raised when the Main Control starts modulation but does not receive a gating acknowledge from the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 676 | V6 FiberCommLoss | V6 Fiber Communication Loss This condition indicates a loss of fiber communication between the XCVR board and the power cell. This is raised when the Main Control starts modulation but does not receive a gating acknowledge from the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 677 | V7 FiberCommLoss | V7 Fiber Communication Loss This condition indicates a loss of fiber communication between the XCVR board and the power cell. This is raised when the Main Control starts modulation but does not receive a gating acknowledge from the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 678 | V8 FiberCommLoss | V8 Fiber Communication Loss This condition indicates a loss of fiber communication between the XCVR board and the power cell. This is raised when the Main Control starts modulation but does not receive a gating acknowledge from the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 680 | W0 FiberCommLoss | W0 Fiber Communication Loss This condition indicates a loss of fiber communication between the XCVR board and the power cell. This is raised when the Main Control starts modulation but does not receive a gating acknowledge from the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 681 | W1 FiberCommLoss | W1 Fiber Communication Loss This condition indicates a loss of fiber communication between the XCVR board and the power cell. This is raised when the Main Control starts modulation but does not receive a gating acknowledge from the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 682 | W2 FiberCommLoss | W2 Fiber Communication Loss This condition indicates a loss of fiber communication between the XCVR board and the power cell. This is raised when the Main Control starts modulation but does not receive a gating acknowledge from the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 683 | W3 FiberCommLoss | W3 Fiber Communication Loss This condition indicates a loss of fiber communication between the XCVR board and the power cell. This is raised when the Main Control starts modulation but does not receive a gating acknowledge from the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 684 | W4 FiberCommLoss | W4 Fiber Communication Loss This condition indicates a loss of fiber communication between the XCVR board and the power cell. This is raised when the Main Control starts modulation but does not receive a gating acknowledge from the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 685 | W5 FiberCommLoss | W5 Fiber Communication Loss This condition indicates a loss of fiber communication between the XCVR board and the power cell. This is raised when the Main Control starts modulation but does not receive a gating acknowledge from the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 686 | W6 FiberCommLoss | W6 Fiber Communication Loss This condition indicates a loss of fiber communication between the XCVR board and the power cell. This is raised when the Main Control starts modulation but does not receive a gating acknowledge from the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 687 | W7 FiberCommLoss | W7 Fiber Communication Loss This condition indicates a loss of fiber communication between the XCVR board and the power cell. This is raised when the Main Control starts modulation but does not receive a gating acknowledge from the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 688 | W8 FiberCommLoss | W8 Fiber Communication Loss This condition indicates a loss of fiber communication between the XCVR board and the power cell. This is raised when the Main Control starts modulation but does not receive a gating acknowledge from the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 690 | U0FWCompatiblity | U0 Power Cell FW Version Incompatible This condition indicates that power cell firmware is not compatible with the power cell hardware. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 691 | U1FWCompatiblity | U1 Power Cell FW Version Incompatible This condition indicates that power cell firmware is not compatible with the power cell hardware. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 692 | U2FWCompatiblity | U2 Power Cell FW Version Incompatible This condition indicates that power cell firmware is not compatible with the power cell hardware. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 693 | U3FWCompatiblity | U3 Power Cell FW Version Incompatible This condition indicates that power cell firmware is not compatible with the power cell hardware. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 694 | U4FWCompatiblity | U4 Power Cell FW Version Incompatible This condition indicates that power cell firmware is not compatible with the power cell hardware. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 695 | U5FWCompatiblity | U5 Power Cell FW Version Incompatible This condition indicates that power cell firmware is not compatible with the power cell hardware. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 696 | U6FWCompatiblity | U6 Power Cell FW Version Incompatible This condition indicates that power cell firmware is not compatible with the power cell hardware. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 697 | U7FWCompatiblity | U7 Power Cell FW Version Incompatible This condition indicates that power cell firmware is not compatible with the power cell hardware. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 698 | U8FWCompatiblity | U8 Power Cell FW Version Incompatible This condition indicates that power cell firmware is not compatible with the power cell hardware. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 700 | V0FWCompatiblity | V0 Power Cell FW Version Incompatible This condition indicates that power cell firmware is not compatible with the power cell hardware. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 701 | V1FWCompatiblity | V1 Power Cell FW Version Incompatible This condition indicates that power cell firmware is not compatible with the power cell hardware. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 702 | V2FWCompatiblity | V2 Power Cell FW Version Incompatible This condition indicates that power cell firmware is not compatible with the power cell hardware. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 703 | V3FWCompatiblity | V3 Power Cell FW Version Incompatible This condition indicates that power cell firmware is not compatible with the power cell hardware. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 704 | V4FWCompatiblity | V4 Power Cell FW Version Incompatible This condition indicates that power cell firmware is not compatible with the power cell hardware. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 705 | V5FWCompatiblity | V5 Power Cell FW Version Incompatible This condition indicates that power cell firmware is not compatible with the power cell hardware. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 706 | V6FWCompatiblity | V6 Power Cell FW Version Incompatible This condition indicates that power cell firmware is not compatible with the power cell hardware. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 707 | V7FWCompatiblity | V7 Power Cell FW Version Incompatible This condition indicates that power cell firmware is not compatible with the power cell hardware. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 708 | V8FWCompatiblity | V8 Power Cell FW Version Incompatible This condition indicates that power cell firmware is not compatible with the power cell hardware. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 710 | W0FWCompatiblity | W0 Power Cell FW Version Incompatible This condition indicates that power cell firmware is not compatible with the power cell hardware. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 711 | W1FWCompatiblity | W1 Power Cell FW Version Incompatible This condition indicates that power cell firmware is not compatible with the power cell hardware. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 712 | W2FWCompatiblity | W2 Power Cell FW Version Incompatible This condition indicates that power cell firmware is not compatible with the power cell hardware. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 713 | W3FWCompatiblity | W3 Power Cell FW Version Incompatible This condition indicates that power cell firmware is not compatible with the power cell hardware. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 714 | W4FWCompatiblity | W4 Power Cell FW Version Incompatible This condition indicates that power cell firmware is not compatible with the power cell hardware. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 715 | W5FWCompatiblity | W5 Power Cell FW Version Incompatible This condition indicates that power cell firmware is not compatible with the power cell hardware. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 716 | W6FWCompatiblity | W6 Power Cell FW Version Incompatible This condition indicates that power cell firmware is not compatible with the power cell hardware. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 717 | W7FWCompatiblity | W7 Power Cell FW Version Incompatible This condition indicates that power cell firmware is not compatible with the power cell hardware. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 718 | W8FWCompatiblity | W8 Power Cell FW Version Incompatible This condition indicates that power cell firmware is not compatible with the power cell hardware. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault | 720 | U0 R/W Error | U0 Read and Write Parameters Failure This condition indicates that an error occurred in either reading or writing a parameter to the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 721 | U1 R/W Error | U1 Read and Write Parameters Failure This condition indicates that an error occurred in either reading or writing a parameter to the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 722 | U2 R/W Error | U2 Read and Write Parameters Failure This condition indicates that an error occurred in either reading or writing a parameter to the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 723 | U3 R/W Error | U3 Read and Write Parameters Failure This condition indicates that an error occurred in either reading or writing a parameter to the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 724 | U4 R/W Error | U4 Read and Write Parameters Failure This condition indicates that an error occurred in either reading or writing a parameter to the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 725 | U5 R/W Error | U5 Read and Write Parameters Failure This condition indicates that an error occurred in either reading or writing a parameter to the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 726 | U6 R/W Error | U6 Read and Write Parameters Failure This condition indicates that an error occurred in either reading or writing a parameter to the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 727 | U7 R/W Error | U7 Read and Write Parameters Failure This condition indicates that an error occurred in either reading or writing a parameter to the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 728 | U8 R/W Error | U8 Read and Write Parameters Failure This condition indicates that an error occurred in either reading or writing a parameter to the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 730 | V0 R/W Error | V0 Read and Write Parameters Failure This condition indicates that an error occurred in either reading or writing a parameter to the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 731 | V1 R/W Error | V1 Read and Write Parameters Failure This condition indicates that an error occurred in either reading or writing a parameter to the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 732 | V2 R/W Error | V2 Read and Write Parameters Failure This condition indicates that an error occurred in either reading or writing a parameter to the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 733 | V3 R/W Error | V3 Read and Write Parameters Failure This condition indicates that an error occurred in either reading or writing a parameter to the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 734 | V4 R/W Error | V4 Read and Write Parameters Failure This condition indicates that an error occurred in either reading or writing a parameter to the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 735 | V5 R/W Error | V5 Read and Write Parameters Failure This condition indicates that an error occurred in either reading or writing a parameter to the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 736 | V6 R/W Error | V6 Read and Write Parameters Failure This condition indicates that an error occurred in either reading or writing a parameter to the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 737 | V7 R/W Error | V7 Read and Write Parameters Failure This condition indicates that an error occurred in either reading or writing a parameter to the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 738 | V8 R/W Error | V8 Read and Write Parameters Failure This condition indicates that an error occurred in either reading or writing a parameter to the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 740 | W0 R/W Error | W0 Read and Write Parameters Failure This condition indicates that an error occurred in either reading or writing a parameter to the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 741 | W1 R/W Error | W1 Read and Write Parameters Failure This condition indicates that an error occurred in either reading or writing a parameter to the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 742 | W2 R/W Error | W2 Read and Write Parameters Failure This condition indicates that an error occurred in either reading or writing a parameter to the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 743 | W3 R/W Error | W3 Read and Write Parameters Failure This condition indicates that an error occurred in either reading or writing a parameter to the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 744 | W4 R/W Error | W4 Read and Write Parameters Failure This condition indicates that an error occurred in either reading or writing a parameter to the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 745 | W5 R/W Error | W5 Read and Write Parameters Failure This condition indicates that an error occurred in either reading or writing a parameter to the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 746 | W6 R/W Error | W6 Read and Write Parameters Failure This condition indicates that an error occurred in either reading or writing a parameter to the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 747 | W7 R/W Error | W7 Read and Write Parameters Failure This condition indicates that an error occurred in either reading or writing a parameter to the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Fault | 748 | W8 R/W Error | W8 Read and Write Parameters Failure This condition indicates that an error occurred in either reading or writing a parameter to the power cell. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Alarm 1 | 750 | U0 Flash Timeout | U0 HSI Flash Timeout This condition indicates that a flash timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 751 | U1 Flash Timeout | U1 HSI Flash Timeout This condition indicates that a flash timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 752 | U2 Flash Timeout | U2 HSI Flash Timeout This condition indicates that a flash timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 753 | U3 Flash Timeout | U3 HSI Flash Timeout This condition indicates that a flash timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 754 | U4 Flash Timeout | U4 HSI Flash Timeout This condition indicates that a flash timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 755 | U5 Flash Timeout | U5 HSI Flash Timeout This condition indicates that a flash timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 756 | U6 Flash Timeout | U6 HSI Flash Timeout This condition indicates that a flash timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 757 | U7 Flash Timeout | U7 HSI Flash Timeout This condition indicates that a flash timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 758 | U8 Flash Timeout | U8 HSI Flash Timeout This condition indicates that a flash timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 760 | V0 Flash Timeout | V0 HSI Flash Timeout This condition indicates that a flash timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 761 | V1 Flash Timeout | V1 HSI Flash Timeout This condition indicates that a flash timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 762 | V2 Flash Timeout | V2 HSI Flash Timeout This condition indicates that a flash timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 763 | V3 Flash Timeout | V3 HSI Flash Timeout This condition indicates that a flash timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 764 | V4 Flash Timeout | V4 HSI Flash Timeout This condition indicates that a flash timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 765 | V5 Flash Timeout | V5 HSI Flash Timeout This condition indicates that a flash timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 766 | V6 Flash Timeout | V6 HSI Flash Timeout This condition indicates that a flash timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 767 | V7 Flash Timeout | V7 HSI Flash Timeout This condition indicates that a flash timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 768 | V8 Flash Timeout | V8 HSI Flash Timeout This condition indicates that a flash timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 770 | W0 Flash Timeout | W0 HSI Flash Timeout This condition indicates that a flash timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 771 | W1 Flash Timeout | W1 HSI Flash Timeout This condition indicates that a flash timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 772 | W2 Flash Timeout | W2 HSI Flash Timeout This condition indicates that a flash timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 773 | W3 Flash Timeout | W3 HSI Flash Timeout This condition indicates that a flash timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 774 | W4 Flash Timeout | W4 HSI Flash Timeout This condition indicates that a flash timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 775 | W5 Flash Timeout | W5 HSI Flash Timeout This condition indicates that a flash timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 776 | W6 Flash Timeout | W6 HSI Flash Timeout This condition indicates that a flash timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 777 | W7 Flash Timeout | W7 HSI Flash Timeout This condition indicates that a flash timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 778 | W8 Flash Timeout | W8 HSI Flash Timeout This condition indicates that a flash timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 780 | U0FlshRstTimeout | U0 HSI Flash Reset Timeout This condition indicates that a flash reset timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 781 | U1FlshRstTimeout | U1 HSI Flash Reset Timeout This condition indicates that a flash reset timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 782 | U2FlshRstTimeout | U2 HSI Flash Reset Timeout This condition indicates that a flash reset timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 783 | U3FlshRstTimeout | U3 HSI Flash Reset Timeout This condition indicates that a flash reset timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 784 | U4FlshRstTimeout | U4 HSI Flash Reset Timeout This condition indicates that a flash reset timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 785 | U5FlshRstTimeout | U5 HSI Flash Reset Timeout This condition indicates that a flash reset timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 786 | U6FlshRstTimeout | U6 HSI Flash Reset Timeout This condition indicates that a flash reset timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 787 | U7FlshRstTimeout | U7 HSI Flash Reset Timeout This condition indicates that a flash reset timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 788 | U8FlshRstTimeout | U8 HSI Flash Reset Timeout This condition indicates that a flash reset timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 790 | V0FlshRstTimeout | V0 HSI Flash Reset Timeout This condition indicates that a flash reset timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 791 | V1FlshRstTimeout | V1 HSI Flash Reset Timeout This condition indicates that a flash reset timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 792 | V2FlshRstTimeout | V2 HSI Flash Reset Timeout This condition indicates that a flash reset timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 793 | V3FlshRstTimeout | V3 HSI Flash Reset Timeout This condition indicates that a flash reset timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 794 | V4FlshRstTimeout | V4 HSI Flash Reset Timeout This condition indicates that a flash reset timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 795 | V5FlshRstTimeout | V5 HSI Flash Reset Timeout This condition indicates that a flash reset timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 796 | V6FlshRstTimeout | V6 HSI Flash Reset Timeout This condition indicates that a flash reset timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 797 | V7FlshRstTimeout | V7 HSI Flash Reset Timeout This condition indicates that a flash reset timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 798 | V8FlshRstTimeout | V8 HSI Flash Reset Timeout This condition indicates that a flash reset timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 800 | W0FlshRstTimeout | W0 HSI Flash Reset Timeout This condition indicates that a flash reset timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 801 | W1FlshRstTimeout | W1 HSI Flash Reset Timeout This condition indicates that a flash reset timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 802 | W2FlshRstTimeout | W2 HSI Flash Reset Timeout This condition indicates that a flash reset timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 803 | W3FlshRstTimeout | W3 HSI Flash Reset Timeout This condition indicates that a flash reset timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 804 | W4FlshRstTimeout | W4 HSI Flash Reset Timeout This condition indicates that a flash reset timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 805 | W5FlshRstTimeout | W5 HSI Flash Reset Timeout This condition indicates that a flash reset timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 806 | W6FlshRstTimeout | W6 HSI Flash Reset Timeout This condition indicates that a flash reset timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 807 | W7FlshRstTimeout | W7 HSI Flash Reset Timeout This condition indicates that a flash reset timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Alarm 1 | 808 | W8FlshRstTimeout | W8 HSI Flash Reset Timeout This condition indicates that a flash reset timeout occurred between the power cell and the main control board during a flash update. | — | — | — | —
Resettable Fault | 810 | U0 DeviceTimeout | U0 Device Message Timeout This condition indicates that the power cell has stopped transmitting messages to the main control board. Power down and then check the fiber optic communication connections. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 811 | U1 DeviceTimeout | U1 Device Message Timeout This condition indicates that the power cell has stopped transmitting messages to the main control board. Power down and then check the fiber optic communication connections. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 812 | U2 DeviceTimeout | U2 Device Message Timeout This condition indicates that the power cell has stopped transmitting messages to the main control board. Power down and then check the fiber optic communication connections. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 813 | U3 DeviceTimeout | U3 Device Message Timeout This condition indicates that the power cell has stopped transmitting messages to the main control board. Power down and then check the fiber optic communication connections. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 814 | U4 DeviceTimeout | U4 Device Message Timeout This condition indicates that the power cell has stopped transmitting messages to the main control board. Power down and then check the fiber optic communication connections. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 815 | U5 DeviceTimeout | U5 Device Message Timeout This condition indicates that the power cell has stopped transmitting messages to the main control board. Power down and then check the fiber optic communication connections. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 816 | U6 DeviceTimeout | U6 Device Message Timeout This condition indicates that the power cell has stopped transmitting messages to the main control board. Power down and then check the fiber optic communication connections. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 817 | U7 DeviceTimeout | U7 Device Message Timeout This condition indicates that the power cell has stopped transmitting messages to the main control board. Power down and then check the fiber optic communication connections. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 818 | U8 DeviceTimeout | U8 Device Message Timeout This condition indicates that the power cell has stopped transmitting messages to the main control board. Power down and then check the fiber optic communication connections. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 820 | V0 DeviceTimeout | V0 Device Message Timeout This condition indicates that the power cell has stopped transmitting messages to the main control board. Power down and then check the fiber optic communication connections. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 821 | V1 DeviceTimeout | V1 Device Message Timeout This condition indicates that the power cell has stopped transmitting messages to the main control board. Power down and then check the fiber optic communication connections. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 822 | V2 DeviceTimeout | V2 Device Message Timeout This condition indicates that the power cell has stopped transmitting messages to the main control board. Power down and then check the fiber optic communication connections. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 823 | V3 DeviceTimeout | V3 Device Message Timeout This condition indicates that the power cell has stopped transmitting messages to the main control board. Power down and then check the fiber optic communication connections. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 824 | V4 DeviceTimeout | V4 Device Message Timeout This condition indicates that the power cell has stopped transmitting messages to the main control board. Power down and then check the fiber optic communication connections. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 825 | V5 DeviceTimeout | V5 Device Message Timeout This condition indicates that the power cell has stopped transmitting messages to the main control board. Power down and then check the fiber optic communication connections. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 826 | V6 DeviceTimeout | V6 Device Message Timeout This condition indicates that the power cell has stopped transmitting messages to the main control board. Power down and then check the fiber optic communication connections. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 827 | V7 DeviceTimeout | V7 Device Message Timeout This condition indicates that the power cell has stopped transmitting messages to the main control board. Power down and then check the fiber optic communication connections. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 828 | V8 DeviceTimeout | V8 Device Message Timeout This condition indicates that the power cell has stopped transmitting messages to the main control board. Power down and then check the fiber optic communication connections. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 830 | W0 DeviceTimeout | W0 Device Message Timeout This condition indicates that the power cell has stopped transmitting messages to the main control board. Power down and then check the fiber optic communication connections. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 831 | W1 DeviceTimeout | W1 Device Message Timeout This condition indicates that the power cell has stopped transmitting messages to the main control board. Power down and then check the fiber optic communication connections. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 832 | W2 DeviceTimeout | W2 Device Message Timeout This condition indicates that the power cell has stopped transmitting messages to the main control board. Power down and then check the fiber optic communication connections. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 833 | W3 DeviceTimeout | W3 Device Message Timeout This condition indicates that the power cell has stopped transmitting messages to the main control board. Power down and then check the fiber optic communication connections. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 834 | W4 DeviceTimeout | W4 Device Message Timeout This condition indicates that the power cell has stopped transmitting messages to the main control board. Power down and then check the fiber optic communication connections. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 835 | W5 DeviceTimeout | W5 Device Message Timeout This condition indicates that the power cell has stopped transmitting messages to the main control board. Power down and then check the fiber optic communication connections. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 836 | W6 DeviceTimeout | W6 Device Message Timeout This condition indicates that the power cell has stopped transmitting messages to the main control board. Power down and then check the fiber optic communication connections. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 837 | W7 DeviceTimeout | W7 Device Message Timeout This condition indicates that the power cell has stopped transmitting messages to the main control board. Power down and then check the fiber optic communication connections. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 838 | W8 DeviceTimeout | W8 Device Message Timeout This condition indicates that the power cell has stopped transmitting messages to the main control board. Power down and then check the fiber optic communication connections. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Alarm 1 | 840 | U0 Login Timeout | U0 HSI Login Timeout This condition indicates that the power cell has failed to login with the main control board after a flash update. | — | — | — | —
Alarm 1 | 841 | U1 Login Timeout | U1 HSI Login Timeout This condition indicates that the power cell has failed to login with the main control board after a flash update. | — | — | — | —
Alarm 1 | 842 | U2 Login Timeout | U2 HSI Login Timeout This condition indicates that the power cell has failed to login with the main control board after a flash update. | — | — | — | —
Alarm 1 | 843 | U3 Login Timeout | U3 HSI Login Timeout This condition indicates that the power cell has failed to login with the main control board after a flash update. | — | — | — | —
Alarm 1 | 844 | U4 Login Timeout | U4 HSI Login Timeout This condition indicates that the power cell has failed to login with the main control board after a flash update. | — | — | — | —
Alarm 1 | 845 | U5 Login Timeout | U5 HSI Login Timeout This condition indicates that the power cell has failed to login with the main control board after a flash update. | — | — | — | —
Alarm 1 | 846 | U6 Login Timeout | U6 HSI Login Timeout This condition indicates that the power cell has failed to login with the main control board after a flash update. | — | — | — | —
Alarm 1 | 847 | U7 Login Timeout | U7 HSI Login Timeout This condition indicates that the power cell has failed to login with the main control board after a flash update. | — | — | — | —
Alarm 1 | 848 | U8 Login Timeout | U8 HSI Login Timeout This condition indicates that the power cell has failed to login with the main control board after a flash update. | — | — | — | —
Alarm 1 | 850 | V0 Login Timeout | V0 HSI Login Timeout This condition indicates that the power cell has failed to login with the main control board after a flash update. | — | — | — | —
Alarm 1 | 851 | V1 Login Timeout | V1 HSI Login Timeout This condition indicates that the power cell has failed to login with the main control board after a flash update. | — | — | — | —
Alarm 1 | 852 | V2 Login Timeout | V2 HSI Login Timeout This condition indicates that the power cell has failed to login with the main control board after a flash update. | — | — | — | —
Alarm 1 | 853 | V3 Login Timeout | V3 HSI Login Timeout This condition indicates that the power cell has failed to login with the main control board after a flash update. | — | — | — | —
Alarm 1 | 854 | V4 Login Timeout | V4 HSI Login Timeout This condition indicates that the power cell has failed to login with the main control board after a flash update. | — | — | — | —
Alarm 1 | 855 | V5 Login Timeout | V5 HSI Login Timeout This condition indicates that the power cell has failed to login with the main control board after a flash update. | — | — | — | —
Alarm 1 | 856 | V6 Login Timeout | V6 HSI Login Timeout This condition indicates that the power cell has failed to login with the main control board after a flash update. | — | — | — | —
Alarm 1 | 857 | V7 Login Timeout | V7 HSI Login Timeout This condition indicates that the power cell has failed to login with the main control board after a flash update. | — | — | — | —
Alarm 1 | 858 | V8 Login Timeout | V8 HSI Login Timeout This condition indicates that the power cell has failed to login with the main control board after a flash update. | — | — | — | —
Alarm 1 | 860 | W0 Login Timeout | W0 HSI Login Timeout This condition indicates that the power cell has failed to login with the main control board after a flash update. | — | — | — | —
Alarm 1 | 861 | W1 Login Timeout | W1 HSI Login Timeout This condition indicates that the power cell has failed to login with the main control board after a flash update. | — | — | — | —
Alarm 1 | 862 | W2 Login Timeout | W2 HSI Login Timeout This condition indicates that the power cell has failed to login with the main control board after a flash update. | — | — | — | —
Alarm 1 | 863 | W3 Login Timeout | W3 HSI Login Timeout This condition indicates that the power cell has failed to login with the main control board after a flash update. | — | — | — | —
Alarm 1 | 864 | W4 Login Timeout | W4 HSI Login Timeout This condition indicates that the power cell has failed to login with the main control board after a flash update. | — | — | — | —
Alarm 1 | 865 | W5 Login Timeout | W5 HSI Login Timeout This condition indicates that the power cell has failed to login with the main control board after a flash update. | — | — | — | —
Alarm 1 | 866 | W6 Login Timeout | W6 HSI Login Timeout This condition indicates that the power cell has failed to login with the main control board after a flash update. | — | — | — | —
Alarm 1 | 867 | W7 Login Timeout | W7 HSI Login Timeout This condition indicates that the power cell has failed to login with the main control board after a flash update. | — | — | — | —
Alarm 1 | 868 | W8 Login Timeout | W8 HSI Login Timeout This condition indicates that the power cell has failed to login with the main control board after a flash update. | — | — | — | —
Alarm 1 | 870 | U0 Flash DPI Err | U0 Flash DPI Error This condition indicates that a DPI error has occurred during a flash update. | — | — | — | —
Alarm 1 | 871 | U1 Flash DPI Err | U1 Flash DPI Error This condition indicates that a DPI error has occurred during a flash update. | — | — | — | —
Alarm 1 | 872 | U2 Flash DPI Err | U2 Flash DPI Error This condition indicates that a DPI error has occurred during a flash update. | — | — | — | —
Alarm 1 | 873 | U3 Flash DPI Err | U3 Flash DPI Error This condition indicates that a DPI error has occurred during a flash update. | — | — | — | —
Alarm 1 | 874 | U4 Flash DPI Err | U4 Flash DPI Error This condition indicates that a DPI error has occurred during a flash update. | — | — | — | —
Alarm 1 | 875 | U5 Flash DPI Err | U5 Flash DPI Error This condition indicates that a DPI error has occurred during a flash update. | — | — | — | —
Alarm 1 | 876 | U6 Flash DPI Err | U6 Flash DPI Error This condition indicates that a DPI error has occurred during a flash update. | — | — | — | —
Alarm 1 | 877 | U7 Flash DPI Err | U7 Flash DPI Error This condition indicates that a DPI error has occurred during a flash update. | — | — | — | —
Alarm 1 | 878 | U8 Flash DPI Err | U8 Flash DPI Error This condition indicates that a DPI error has occurred during a flash update. | — | — | — | —
Alarm 1 | 880 | V0 Flash DPI Err | V0 Flash DPI Error This condition indicates that a DPI error has occurred during a flash update. | — | — | — | —
Alarm 1 | 881 | V1 Flash DPI Err | V1 Flash DPI Error This condition indicates that a DPI error has occurred during a flash update. | — | — | — | —
Alarm 1 | 882 | V2 Flash DPI Err | V2 Flash DPI Error This condition indicates that a DPI error has occurred during a flash update. | — | — | — | —
Alarm 1 | 883 | V3 Flash DPI Err | V3 Flash DPI Error This condition indicates that a DPI error has occurred during a flash update. | — | — | — | —
Alarm 1 | 884 | V4 Flash DPI Err | V4 Flash DPI Error This condition indicates that a DPI error has occurred during a flash update. | — | — | — | —
Alarm 1 | 885 | V5 Flash DPI Err | V5 Flash DPI Error This condition indicates that a DPI error has occurred during a flash update. | — | — | — | —
Alarm 1 | 886 | V6 Flash DPI Err | V6 Flash DPI Error This condition indicates that a DPI error has occurred during a flash update. | — | — | — | —
Alarm 1 | 887 | V7 Flash DPI Err | V7 Flash DPI Error This condition indicates that a DPI error has occurred during a flash update. | — | — | — | —
Alarm 1 | 888 | V8 Flash DPI Err | V8 Flash DPI Error This condition indicates that a DPI error has occurred during a flash update. | — | — | — | —
Alarm 1 | 890 | W0 Flash DPI Err | W0 Flash DPI Error This condition indicates that a DPI error has occurred during a flash update. | — | — | — | —
Alarm 1 | 891 | W1 Flash DPI Err | W1 Flash DPI Error This condition indicates that a DPI error has occurred during a flash update. | — | — | — | —
Alarm 1 | 892 | W2 Flash DPI Err | W2 Flash DPI Error This condition indicates that a DPI error has occurred during a flash update. | — | — | — | —
Alarm 1 | 893 | W3 Flash DPI Err | W3 Flash DPI Error This condition indicates that a DPI error has occurred during a flash update. | — | — | — | —
Alarm 1 | 894 | W4 Flash DPI Err | W4 Flash DPI Error This condition indicates that a DPI error has occurred during a flash update. | — | — | — | —
Alarm 1 | 895 | W5 Flash DPI Err | W5 Flash DPI Error This condition indicates that a DPI error has occurred during a flash update. | — | — | — | —
Alarm 1 | 896 | W6 Flash DPI Err | W6 Flash DPI Error This condition indicates that a DPI error has occurred during a flash update. | — | — | — | —
Alarm 1 | 897 | W7 Flash DPI Err | W7 Flash DPI Error This condition indicates that a DPI error has occurred during a flash update. | — | — | — | —
Alarm 1 | 898 | W8 Flash DPI Err | W8 Flash DPI Error This condition indicates that a DPI error has occurred during a flash update. | — | — | — | —
Fault | 900 | U0 Login Failure | U0 Login Failure This condition indicates that the PCCB failed to send Login data to ICB. | — | — | — | —
Fault | 901 | U1 Login Failure | U1 Login Failure This condition indicates that the PCCB failed to send Login data to ICB. | — | — | — | —
Fault | 902 | U2 Login Failure | U2 Login Failure This condition indicates that the PCCB failed to send Login data to ICB. | — | — | — | —
Fault | 903 | U3 Login Failure | U3 Login Failure This condition indicates that the PCCB failed to send Login data to ICB. | — | — | — | —
Fault | 904 | U4 Login Failure | U4 Login Failure This condition indicates that the PCCB failed to send Login data to ICB. | — | — | — | —
Fault | 905 | U5 Login Failure | U5 Login Failure This condition indicates that the PCCB failed to send Login data to ICB. | — | — | — | —
Fault | 906 | U6 Login Failure | U6 Login Failure This condition indicates that the PCCB failed to send Login data to ICB. | — | — | — | —
Fault | 907 | U7 Login Failure | U7 Login Failure This condition indicates that the PCCB failed to send Login data to ICB. | — | — | — | —
Fault | 908 | U8 Login Failure | U8 Login Failure This condition indicates that the PCCB failed to send Login data to ICB. | — | — | — | —
Fault | 910 | V0 Login Failure | V0 Login Failure This condition indicates that the PCCB failed to send Login data to ICB. | — | — | — | —
Fault | 911 | V1 Login Failure | V1 Login Failure This condition indicates that the PCCB failed to send Login data to ICB. | — | — | — | —
Fault | 912 | V2 Login Failure | V2 Login Failure This condition indicates that the PCCB failed to send Login data to ICB. | — | — | — | —
Fault | 913 | V3 Login Failure | V3 Login Failure This condition indicates that the PCCB failed to send Login data to ICB. | — | — | — | —
Fault | 914 | V4 Login Failure | V4 Login Failure This condition indicates that the PCCB failed to send Login data to ICB. | — | — | — | —
Fault | 915 | V5 Login Failure | V5 Login Failure This condition indicates that the PCCB failed to send Login data to ICB. | — | — | — | —
Fault | 916 | V6 Login Failure | V6 Login Failure This condition indicates that the PCCB failed to send Login data to ICB. | — | — | — | —
Fault | 917 | V7 Login Failure | V7 Login Failure This condition indicates that the PCCB failed to send Login data to ICB. | — | — | — | —
Fault | 918 | V8 Login Failure | V8 Login Failure This condition indicates that the PCCB failed to send Login data to ICB. | — | — | — | —
Fault | 920 | W0 Login Failure | W0 Login Failure This condition indicates that the PCCB failed to send Login data to ICB. | — | — | — | —
Fault | 921 | W1 Login Failure | W1 Login Failure This condition indicates that the PCCB failed to send Login data to ICB. | — | — | — | —
Fault | 922 | W2 Login Failure | W2 Login Failure This condition indicates that the PCCB failed to send Login data to ICB. | — | — | — | —
Fault | 923 | W3 Login Failure | W3 Login Failure This condition indicates that the PCCB failed to send Login data to ICB. | — | — | — | —
Fault | 924 | W4 Login Failure | W4 Login Failure This condition indicates that the PCCB failed to send Login data to ICB. | — | — | — | —
Fault | 925 | W5 Login Failure | W5 Login Failure This condition indicates that the PCCB failed to send Login data to ICB. | — | — | — | —
Fault | 926 | W6 Login Failure | W6 Login Failure This condition indicates that the PCCB failed to send Login data to ICB. | — | — | — | —
Fault | 927 | W7 Login Failure | W7 Login Failure This condition indicates that the PCCB failed to send Login data to ICB. | — | — | — | —
Fault | 928 | W8 Login Failure | W8 Login Failure This condition indicates that the PCCB failed to send Login data to ICB. | — | — | — | —
Fault | 930 | U0 FW Mismatch | U0 FW Mismatch This condition indicates that the PCCB firmware did not match with the DPI file in the NVS. | — | — | — | —
Fault | 931 | U1 FW Mismatch | U1 FW Mismatch This condition indicates that the PCCB firmware did not match with the DPI file in the NVS. | — | — | — | —
Fault | 932 | U2 FW Mismatch | U2 FW Mismatch This condition indicates that the PCCB firmware did not match with the DPI file in the NVS. | — | — | — | —
Fault | 933 | U3 FW Mismatch | U3 FW Mismatch This condition indicates that the PCCB firmware did not match with the DPI file in the NVS. | — | — | — | —
Fault | 934 | U4 FW Mismatch | U4 FW Mismatch This condition indicates that the PCCB firmware did not match with the DPI file in the NVS. | — | — | — | —
Fault | 935 | U5 FW Mismatch | U5 FW Mismatch This condition indicates that the PCCB firmware did not match with the DPI file in the NVS. | — | — | — | —
Fault | 936 | U6 FW Mismatch | U6 FW Mismatch This condition indicates that the PCCB firmware did not match with the DPI file in the NVS. | — | — | — | —
Fault | 937 | U7 FW Mismatch | U7 FW Mismatch This condition indicates that the PCCB firmware did not match with the DPI file in the NVS. | — | — | — | —
Fault | 938 | U8 FW Mismatch | U8 FW Mismatch This condition indicates that the PCCB firmware did not match with the DPI file in the NVS. | — | — | — | —
Fault | 940 | V0 FW Mismatch | V0 FW Mismatch This condition indicates that the PCCB firmware did not match with the DPI file in the NVS. | — | — | — | —
Fault | 941 | V1 FW Mismatch | V1 FW Mismatch This condition indicates that the PCCB firmware did not match with the DPI file in the NVS. | — | — | — | —
Fault | 942 | V2 FW Mismatch | V2 FW Mismatch This condition indicates that the PCCB firmware did not match with the DPI file in the NVS. | — | — | — | —
Fault | 943 | V3 FW Mismatch | V3 FW Mismatch This condition indicates that the PCCB firmware did not match with the DPI file in the NVS. | — | — | — | —
Fault | 944 | V4 FW Mismatch | V4 FW Mismatch This condition indicates that the PCCB firmware did not match with the DPI file in the NVS. | — | — | — | —
Fault | 945 | V5 FW Mismatch | V5 FW Mismatch This condition indicates that the PCCB firmware did not match with the DPI file in the NVS. | — | — | — | —
Fault | 946 | V6 FW Mismatch | V6 FW Mismatch This condition indicates that the PCCB firmware did not match with the DPI file in the NVS. | — | — | — | —
Fault | 947 | V7 FW Mismatch | V7 FW Mismatch This condition indicates that the PCCB firmware did not match with the DPI file in the NVS. | — | — | — | —
Fault | 948 | V8 FW Mismatch | V8 FW Mismatch This condition indicates that the PCCB firmware did not match with the DPI file in the NVS. | — | — | — | —
Fault | 950 | W0 FW Mismatch | W0 FW Mismatch This condition indicates that the PCCB firmware did not match with the DPI file in the NVS. | — | — | — | —
Fault | 951 | W1 FW Mismatch | W1 FW Mismatch This condition indicates that the PCCB firmware did not match with the DPI file in the NVS. | — | — | — | —
Fault | 952 | W2 FW Mismatch | W2 FW Mismatch This condition indicates that the PCCB firmware did not match with the DPI file in the NVS. | — | — | — | —
Fault | 953 | W3 FW Mismatch | W3 FW Mismatch This condition indicates that the PCCB firmware did not match with the DPI file in the NVS. | — | — | — | —
Fault | 954 | W4 FW Mismatch | W4 FW Mismatch This condition indicates that the PCCB firmware did not match with the DPI file in the NVS. | — | — | — | —
Fault | 955 | W5 FW Mismatch | W5 FW Mismatch This condition indicates that the PCCB firmware did not match with the DPI file in the NVS. | — | — | — | —
Fault | 956 | W6 FW Mismatch | W6 FW Mismatch This condition indicates that the PCCB firmware did not match with the DPI file in the NVS. | — | — | — | —
Fault | 957 | W7 FW Mismatch | W7 FW Mismatch This condition indicates that the PCCB firmware did not match with the DPI file in the NVS. | — | — | — | —
Fault | 958 | W8 FW Mismatch | W8 FW Mismatch This condition indicates that the PCCB firmware did not match with the DPI file in the NVS. | — | — | — | —
Event | 959 | PC Rplc Ack | Power Cell Replacement Acknowledge This event indicates that the user has acknowledged the replacement alarm for the power cell. | — | — | — | —

## Port 13
Condition Type | Condition Code | Display Text | Fault | Action | Fault Action | Configuration Parameter | Configurable Action
none | 0 | No Entry
Configurable | 1 | LnSyncLoss Det | Loss of PLL Synchronization Detected The line side converter has detected a loss of phase synchronization with the incoming line. | Check line conditions and the configuration of the line side converter control. Check the fuses in the FD1 fused disconnect. | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | 13:181 [PLL LOS Det Actn] | —
Configurable | 3 | Phase Loss Det | Input Phase Loss Detected The RMS value for phase input voltage is less than 15% of the value of parameter 13:25 [Rated Volts]. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | 13:176 [LSCPhLossDet Actn] | —
Configurable | 5 | PowerLoss Det | Power Loss Detected The RMS value for each of the three line-to-line input voltages is less than 15% of the value of parameter 13:25 [Rated Volts]. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | 13:170 [PwrLoss Det Actn] | —
Configurable | 7 | Line Sag Det | Voltage Sag Detected The difference between the instantaneous value of the input AC line voltage and a filtered AC line voltage exceeds 50% of the nominal AC line voltage. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | 13:173 [VltgSag Det Actn] | —
Configurable | 9 | High df/dt Det | High df/dt Detected The input AC line frequency rate of change has exceeded 628.3 radians/second (equivalent to 100 Hz/second). | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | 13:179 [DFDT Det Actn] | —
Alarm 1 | 11 | LineVltgUnbal | Voltage unbalance The absolute value of the difference between any AC line voltage (parameters 13:3 [R-S Line Volts], 13:4 [S-T Line Volts], or 13:5 [T-R Line Volts]) and the total 3-phase average AC line voltage (parameter 13:2 [AC Line Voltage]) exceeded the value of parameter 13:185 [Line V Unbal Lmt] for a time at least the value of parameter 13:186 [Line V Unbal Dly]. | Monitor input AC sine wave for power disturbance. Address disturbance or use ride through function if possible. | — | 13:185 [Line V Unbal Lmt] 13:186 [Line V Unbal Dly] | —
Alarm 1 | 12 | LineCurUnbal | Current unbalance The absolute value of the difference between any AC line current (parameters 13:9 [R Phase Current], 13:10 [S Phase Current], or 13:11 [T Phase Current]) and the average measured RMS AC phase current (parameter 13:6 [AC Line Current]) exceeded the value of parameter 13:188 [Line I Unbal Lmt] for a time at least the value of parameter 13:189 [Line I Unbal Dly]. | Monitor input AC sine wave for power disturbance. Address disturbance or use ride through function if possible. | — | 13:188 [Line I Unbal Lmt] 13:189 [Line I Unbal Dly] | —
Configurable | 13 | AC L12 OvrVltg A | AC Source Over Voltage-L12 > Over A The value of parameter 13:3 [R-S Line Volts] > (13:119 [Over Volt Lmt A] x 13:25 [Rated Volts]) for a time at least parameter 13:120 [Over Volt Dly A] when parameter 13:31 [AC Line Source] is set to 0 ‘AC Line A’. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | 13:121 [OverVltLmtAAc tn] | —
Configurable | 14 | AC L23 OvrVltg A | AC Source Over voltage-L23 > Over A The value of parameter 13:4 [S-T Line Volts] > (13:119 [Over Volt Lmt A] x 13:25 [Rated Volts]) for a time at least parameter 13:120 [Over Volt Dly A] when parameter 13:31 [AC Line Source] is set to 0 ‘AC Line A’. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | 13:121 [OverVltLmtAAc tn] | —
Configurable | 15 | AC L31 OvrVltg A | AC Source Over Voltage-L31 > Over A The value of parameter 13:5 [T-R Line Volts] > (13:119 [Over Volt Lmt A] x 13:25 [Rated Volts]) for a time at least parameter 13:120 [Over Volt Dly A] when parameter 13:31 [AC Line Source] is set to 0 ‘AC Line A’. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | 13:121 [OverVltLmtAAc tn] | —
Configurable | 16 | AC L12 OvrVltg B | AC Source Over Voltage-L12 > Over B The value of parameter 13:3 [R-S Line Volts] > (13:133 [Over Volt Lmt B] x 13:25 [Rated Volts]) for a time at least parameter 13:134 [Over Volt Dly B] when parameter 13:31 [AC Line Source] is set to 1 ‘AC Line B’. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | 13:135 [OverVltLmtBAc tn] | —
Configurable | 17 | AC L23 OvrVltg B | AC Source Over Voltage-L23 > Over B The value of parameter 13:4 [S-T Line Volts] > (13:133 [Over Volt Lmt B] x 13:25 [Rated Volts]) for a time at least parameter 13:134 [Over Volt Dly B] when parameter 13:31 [AC Line Source] is set to 1 ‘AC Line B’. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | 13:135 [OverVltLmtBAc tn] | —
Configurable | 18 | AC L31 OvrVltg B | AC Source Over Voltage-L31 > Over B The value of parameter 13:5 [T-R Line Volts] > (13:133 [Over Volt Lmt B] x 13:25 [Rated Volts]) for a time at least parameter 13:134 [Over Volt Dly B] when parameter 13:31 [AC Line Source] is set to 1 ‘AC Line B’. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | 13:135 [OverVltLmtBAc tn] | —
Configurable | 19 | AC L12 UndrVltgA | AC Source Under Voltage-L12 < Under A The value of parameter 13:3 [R-S Line Volts] < (13:110 [Under Volt Lmt A] x 13:25 [Rated Volts]) for a time at least parameter 13:111 [Under Volt Dly A] when parameter 13:31 [AC Line Source] is set to 0 ‘AC Line A’. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | 13:112 [UnderVltLmtA Actn] | —
Configurable | 20 | AC L23 UndrVltgA | AC Source Under Voltage-L23 < Under A The value of parameter 13:4 [S-T Line Volts] < (13:110 [Under Volt Lmt A] x 13:25 [Rated Volts]) for a time at least parameter 13:120 [Under Volt Dly A] when parameter 13:31 [AC Line Source] is set to 0 ‘AC Line A’. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | 13:112 [UnderVltLmtA Actn] | —
Configurable | 21 | AC L31 UndrVltgA | AC Source Under Voltage-L31 < Under A The value of parameter 13:5 [T-R Line Volts] < (13:110 [Under Volt Lmt A] x 13:25 [Rated Volts]) for a time at least parameter 13:120 [Over Volt Dly A] when parameter 13:31 [AC Line Source] is set to 0 ‘AC Line A’. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | 13:112 [UnderVltLmtA Actn] | —
Configurable | 22 | AC L12 UndrVltgB | AC Source Under Voltage-L12 < Under B The value of parameter 13:3 [R-S Line Volts] < (13:124 [Under Volt Lmt B] x 13:25 [Rated Volts]) for a time at least parameter 13:125 [Under Volt Dly B] when parameter 13:31 [AC Line Source] is set to 1 ‘AC Line B’. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | 13:126 [UnderVltLmtB Actn] | —
Configurable | 23 | AC L23 UndrVltgB | AC Source Under Voltage-L23 < Under B The value of parameter 13:4 [S-T Line Volts] < (13:124 [Under Volt Lmt B] x 13:25 [Rated Volts]) for a time at least parameter 13:125 [Under Volt Dly B]when parameter 13:31 [AC Line Source] is set to 1 ‘AC Line B’. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | 13:126 [UnderVltLmtB Actn] | —
Configurable | 24 | AC L31 UndrVltgB | AC Source Under Voltage-L31 < Under B The value of parameter 13:5 [T-R Line Volts] < (13:124 [Under Volt Lmt B] x 13:25 [Rated Volts]) for a time at least parameter 13:125 [Under Volt Dly B] when parameter 13:31 [AC Line Source] is set to 1 ‘AC Line B’. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | 13:126 [UnderVltLmtB Actn] | —
Configurable | 25 | AC L12 HiVltg A | AC Source High Voltage-L12 > High A The value of parameter 13:3 [R-S Line Volts] > (13:119 [High Volt Lmt A] x 13:25 [Rated Volts]) for a time at least parameter 13:117 [High Volt Dly A] when parameter 13:31 [AC Line Source] is set to 0 ‘AC Line A’. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | 13:118 [HighVltLmtAA ctn] | —
Configurable | 26 | AC L23 HiVltg A | AC source high voltage-L23 > High A The value of parameter 13:4 [S-T Line Volts] > (13:119 [High Volt Lmt A] x 13:25 [Rated Volts]) for a time at least parameter 13:117 [High Volt Dly A] when parameter 13:31 [AC Line Source] is set to 0 ‘AC Line A’. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | 13:118 [HighVltLmtAA ctn] | —
Configurable | 27 | AC L31 HiVltg A | AC Source High Voltage-L31 > High A The value of parameter 13:5 [T-R Line Volts] > (13:119 [High Volt Lmt A] x 13:25 [Rated Volts]) for a time at least parameter 13:117 [High Volt Dly A] when parameter 13:31 [AC Line Source] is set to 0 ‘AC Line A’. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | 13:118 [HighVltLmtAA ctn] | —
Configurable | 28 | AC L12 HiVltg B | AC Source High Voltage-L12 > High B The value of parameter 13:3 [R-S Line Volts] < (13:130 [High Volt Lmt B] x 13:25 [Rated Volts]) for a time at least parameter 13:131 [High Volt Dly B] when parameter 13:31 [AC Line Source] is set to 1 ‘AC Line B’. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | 13:132 [HighVltLmtBAc tn] | —
Configurable | 29 | AC L23 HiVltg B | AC Source High Voltage-L23 > High B The value of parameter 13:4 [S-T Line Volts] < (13:130 [High Volt Lmt B] x 13:25 [Rated Volts]) for a time at least parameter 13:125 [Under Volt Dly B] when parameter 13:31 [AC Line Source] is set to 1 ‘AC Line B’. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | 13:132 [HighVltLmtBAc tn] | —
Configurable | 30 | AC L31 HiVltg B | AC Source High Voltage-L31 > High B The value of parameter 13:5 [T-R Line Volts] < (13:130 [High Volt Lmt B] x 13:25 [Rated Volts]) for a time at least parameter 13:125 [Under Volt Dly B] when parameter 13:31 [AC Line Source] is set to 1 ‘AC Line B’. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | 13:132 [HighVltLmtBAc tn] | —
Configurable | 31 | AC L12 LoVltg A | AC Source Low Voltage-L12 < Low A The value of parameter 13:3 [R-S Line Volts] < (13:113 [Low Volt Lmt A] x 13:25 [Rated Volts]) for a time at least parameter 13:114 [Low Volt Dly A] when parameter 13:31 [AC Line Source] is set to 0 ‘AC Line A’. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | 13:115 [LowVltLmtAAc tn] | —
Configurable | 32 | AC L23 LoVltg A | AC Source Low Voltage-L23 < Low A The value of parameter 13:4 [S-T Line Volts] < (13:113 [Low Volt Lmt A] x 13:25 [Rated Volts]) for a time at least paramter 13:114 [Low Volt Dly A] when parameter 13:31 [AC Line Source] is set to 0 ‘AC Line A’. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | 13:115 [LowVltLmtAAc tn] | —
Configurable | 33 | AC L31 LoVltg A | AC Source Low Voltage-L31 < Low A The value of parameter 13:5 [T-R Line Volts] < (13:113 [Low Volt Lmt A] x 13:25 [Rated Volts]) for a time at least parameter 13:114 [Low Volt Dly A] when parameter 13:31 [AC Line Source] is set to 0 ‘AC Line A’. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | 13:115 [LowVltLmtAAc tn] | —
Configurable | 34 | AC L12 LoVltg B | AC Source Low Voltage-L12 < Low B The value of parameter 13:3 [R-S Line Volts] < (13:127 [Low Volt Lmt B] x 13:25 [Rated Volts]) for a time at least parameter 13:128 [Low Volt Dly B] when parameter 13:31 [AC Line Source] is set to 1 ‘AC Line B’. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | 13:129 [LowVltLmtBAc tn] | —
Configurable | 35 | AC L23 LoVltg B | AC Source Low Voltage-L23 < Low B The value of parameter 13:4 [S-T Line Volts] < (13:127 [Low Volt Lmt B] x 13:25 [Rated Volts]) for a time at least parameter 13:128 [Low Volt Dly B] when parameter 13:31 [AC Line Source] is set to 1 ‘AC Line B’. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | 13:129 [LowVltLmtBAc tn] | —
Configurable | 36 | AC L31 LoVltg B | AC Source Low Voltage-L31 < Low B The value of parameter 13:5 [T-R Line Volts] < (13:127 [Low Volt Lmt B] x 13:25 [Rated Volts]) for a time at least parameter 13:128 [Low Volt Dly B] when parameter 13:31 [AC Line Source] is set to 1 ‘AC Line B’. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | 13:129 [LowVltLmtBAc tn] | —
Configurable | 37 | AC Line OvrFreqA | AC Source Over Frequency - Freq > Over A The value of parameter 13:1 [AC Line Freq] > (13:30 [Nom Line Freq] + 13:149 [Over Freq Lmt A]) for a time at least parameter 13:150 [Over Freq Dly A] when parameter 13:31 [AC Line Source] is set to 0 ‘AC Line A’. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | 13:151 [OverFreqLmtA Actn] | —
Configurable | 38 | AC Line OvrFreqB | AC Source Over Frequency - Freq > Over B The value of parameter 13:1 [AC Line Freq] > (13:30 [Nom Line Freq] x 13:163 [Over Freq Lmt B]) for a time at least parameter 13:165 [Over Freq Dly B] when parameter 13:31 [AC Line Source] is set to 1 ‘AC Line B’. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | 13:165 [OverFreqLmtB Actn] | —
Configurable | 39 | AC Ln UndrFreq A | AC Source Under Frequency - Freq < Under A The value of parameter 13:1 [AC Line Freq] < (13:30 [Nom Line Freq] - 13:140 [Under Freq Lmt A]) for a time at least parameter 13:141 [Under Freq Dly A] when parameter 13:31 [AC Line Source] is set to 0 ‘AC Line A’. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | 13:142 [UnderFreqLmt AActn] | —
Configurable | 40 | AC Ln UndrFreq B | AC Source Under Frequency - Freq < Under B The value of parameter 13:1 [AC Line Freq] < (13:30 [Nom Line Freq] - 13:154 [Under Freq Lmt B]) for a time at least parameter 13:155 [Under Freq Dly B] when parameter 13:31 [AC Line Source] is set to 1 ‘AC Line B’. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | 13:156 [UnderFreqLmt BActn] | —
Configurable | 41 | AC Ln HiFreq A | AC Source High Frequency - Freq > High A The value of parameter 13:1 [AC Line Freq] > (13:30 [Nom Line Frq] + 13:146 [High Freq Lmt A]) for a time at least parameter 13:147 [High Freq Dly A] when parameter 13:31 [AC Line Source] is set to 0 ‘AC Line A’. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | 13:148 [HighFreqLmtA Actn] | —
Configurable | 42 | AC Ln HiFreq B | AC Source High Frequency - Freq > High B The value of parameter 13:1 [AC Line Freq] > (13:30 [Nom Line Frq] + 13:160 [High Freq Lmt B]) for a time at least parameter 13:161 [High Freq Dly B] when parameter 13:31 [AC Line Source] is set to 1 ‘AC Line B’. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | 13:162 [HighFreqLmtB Actn] | —
Configurable | 43 | AC Ln LoFreq A | AC Source Low Frequency - Freq < Low A The value of parameter 13:1 [AC Line Freq] < (13:30 [Nom Line Frq] - 13:143 [Low Freq Lmt A]) for a time at least parameter 13:145 [Low Freq Dly A] when parameter 13:31 [AC Line Source] is set to 0 ‘AC Line A’. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | 13:145 [LowFreqLmtA Actn] | —
Configurable | 44 | AC Ln LoFreq B | AC Source Low Frequency - Freq < Low B The value of parameter 13:1 [AC Line Freq] < (13:30 [Nom Line Frq] - 13:157 [Low Freq Lmt B]) for a time at least parameter 13:158 [Low Freq Dly B] when parameter 13:31 [AC Line Source] is set to 1 ‘AC Line B’. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | 13:159 [LowFreqLmtBA ctn] | —
Configurable | 47 | L Ground Warning | Converter Ground Warning The ground current has exceeded the level set in 0:423 [L Gnd Warn Lvl]. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | 0:422 [L Gnd Warn Actn] | —
Alarm 1 | 50 | Line Phase Rvs | ACB Phase Connection Negative phase connection has been detected in the AC line input. This condition leads to false phase indication in troubleshooting. It does not affect the operating functions of the line side converter. | Power down and reconnect the incoming AC power so the phase rotation is positive. | — | 13:40 [Conv Options Cfg] Bit 0 ‘PhaseRevAlm’ | —
Alarm 1 | 51 | Fdbk Data Late | Control Feedback data arrived late from SFIB The Control Feedback data arrived to the main control board late from power peripherals and Fiber Interface Board (FIB). | — | — | — | —
Resettable Fault | 53 | HW OverCurrent | Hardware Over Current The input current has exceeded the hardware current limit. | — | Stop Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 54 | 125us Task Ovr | 125us Task Overrun The 125-microsecond task has overrun the allotted time. | Clear faults. If the fault persists, run firmware update. If the fault persists, replace the main control board. | Stop Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 55 | 250us Task Ovr | 250us Task Overrun The 250-microsecond task has overrun the allotted time. | Clear faults. If the fault persists, run firmware update. If the fault persists, replace the main control board. | Stop Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 56 | 1ms Task Ovr | 1ms Task Overrun The 1-millisecond task has overrun the allotted time. | Clear faults. If the fault persists, run firmware update. If the fault persists, replace the main control board. | Stop Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 57 | 2ms Task Ovr | 2ms Task Overrun The 2-millisecond task has overrun the allotted time. | Clear faults. If the fault persists, run firmware update. If the fault persists, replace the main control board. | Stop Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 58 | 10ms Task Ovr | 10ms Task Overrun The 10-millisecond task has overrun the allotted time. | Clear faults. If the fault persists, run firmware update. If the fault persists, replace the main control board. | Stop Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 60 | CntrlTask Wtchdg | Control Task Watchdog The Control task has failed to complete in the allotted amount of time. | Clear faults. If the fault persists, run firmware update. If the fault persists, replace the main control board. | Stop Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 61 | SystmTask Wtchdg | System Task Watchdog The System task has failed to complete in the allotted amount of time. | Clear faults. If the fault persists, run firmware update. If the fault persists, replace the main control board. | Stop Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 62 | 1ms Task Wtchdg | 1ms Task Watchdog The 1-millisecond task has failed to complete in the allotted amount of time. | Clear faults. If the fault persists, run firmware update. If the fault persists, replace the main control board. | Stop Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 63 | 2ms Task Wtchdg | 2ms Task Watchdog The 2-millisecond task has failed to complete in the allotted amount of time. | Clear faults. If the fault persists, run firmware update. If the fault persists, replace the main control board. | Stop Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 64 | 10ms Task Wtchdg | 10ms Task Watchdog The 10-millisecond task has failed to complete in the allotted amount of time. | Clear faults. If the fault persists, run firmware update. If the fault persists, replace the main control board. | Stop Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 65 | SW Bus Low Volt | Software Bus Low Voltage An undervoltage condition has occurred. Bus voltage in parameter 0:3 [DC Bus Volts] has fallen below 80% of the peak value of parameter 13:21 [ACLineMemory]. | Verify input voltage is within specification. | Stop (Line Side Converter) Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 1 ‘LS Pwr Flts’ | — | —
Non- Resettable Fault | 67 | Cnv App No Strt | Converter Application Not Start The line side converter application failed to start in the DSP. | Cycle power. If the fault persists, run firmware update. If the fault persists, replace the main control board. | — Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 68 | SW Bus Over Volt | Software Bus Over Voltage The DC bus voltage in 0:3 [DC Bus Volts] exceeded 1130V. | — | Stop Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 1 ‘LS Pwr Flts’ | — | —
Resettable Fault | 75 | Bus Rate of Rise | Bus Rate of Rise Rate of increase in DC bus voltage during precharge is less than expected. Possible causes include a short circuit in the DC bus. | Power down and examine the electrical characteristics of the DC bus and the equipment that is connected to the DC bus. | Stop Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 1 ‘LS Pwr Flts’ | — | —
Alarm 1 | 85 | No LineVltgDtctd | No Line Voltage Detected Input Closed This condition indicates that no line voltage has been detected by the drive with a closed Main/Input device. | — | — | — | —
Resettable Fault | 92 | SW OverCurrent | Software Over Current Line side converter current has exceeded the 1 ms current rating. This rating is greater than the current rating for 3 seconds and less than the hardware overcurrent fault level. It is typically 200…250% of the drive continuous rating. | — | Stop Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 0 ‘LS Ctrl Flts’ | — | —
Alarm 1 | 95 | In Prchrg CycLmt | In Precharge Thermal Cycle Limit This condition indicates that the drive is in a Pre-Charge thermal cycle limit. Review parameter 13:1019 [PrchrgCycLimTmr]. The minimum interval between two consecutive precharge cycles is 80 seconds. | — | — | — | —
Fault Major | 193 | VltgDtctdInpOpen | Line Voltage Detected with Input Open This condition indicates that line voltage was detected with an open Main/Input device. | — | Coast Stop Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —

## Port 14
Condition Type | Condition Code | Display Text | Fault | Action | Fault Action | Configuration Parameter | Configurable Action
none | 0 | No Entry
Resettable Fault | 1 | Image Wtchdg Flt | Image Watchdog Fault Communication between the main control board and the image buffer in the Power IO Board (PIOB) has stopped transmitting for 10 milliseconds. | Power down and then check the fiber-optic communication connections. | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 2 | ConstantsMsgIvld | Constants Message Invalid Fault The constants header information did not match the content expected by the Power IO Board (PIOB). | Cycle power. | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Non-Resettable Fault | 3 | Constants Chksum | Constants Checksum Fault The constants download failed the checksum test by the Power IO Board (PIOB). | Cycle power. | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Resettable Fault | 103 | Device Timeout | Device Message Timeout This condition indicates that the Power IO Board (PIOB) has stopped transmitting messages to the main control board. | Power down and then check the fiber-optic communication connections. | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Alarm 1 | 131 | Flash Timeout | HSI Flash Timeout This condition indicates that an update timeout occurred between Power IO Board (PIOB) and the main control board during a firmware update. | — | — | — | —
Alarm 1 | 132 | FlashRst Timeout | HSI Flash Reset Timeout This condition indicates that an update reset timeout occurred between Power IO Board (PIOB) and the main control board during a firmware update. | — | — | — | —
Alarm 1 | 133 | Login Timeout | HSI Login Timeout This condition indicates that the Power IO Board (PIOB) has failed to login with the main control board after a firmware update. | — | — | — | —
Alarm 1 | 134 | Flash DPI Error | Flash DPI Error This condition Indicates that a DPI error has occurred during a firmware update of the Power IO Board (PIOB). | — | — | — | —
Alarm 1 | 153 | Ctrl PowerLoss | Control Power Loss This condtion occurs five cycles after the AC Control Power Loss event has been detected, if the drive is not running. | — | — | — | —
Configurable | 156 | UPS Failure | UPS Failure This condition is raised when the UPS has detected a fault and disabled its output. This is indicated by the diagnostic signal coming from the UPS. The action taken by the drive is configured by 14:19 [UPS Failure Actn]. | Check the UPS connection, then restart. If the condition persists, refer to the troubleshooting manual. | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 4 ‘PERIFl Flts’ | 14:19 [UPS Failure Actn] | —
Configurable | 157 | UPS on Bypass | UPS on Bypass This condition is raised when the UPS switches to Bypass mode, as indicated by the diagnostic signal from the UPS. The action taken by the drive is configured by 14:22 [UPS Bypass Actn]. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 4 ‘PERIFl Flts’ | 14:22 [UPS Bypass Actn] | —
Configurable | 158 | UPS on Battery | UPS on Battery This condition is raised when the UPS switches to internal battery, as indicated by the diagnostic signal from the UPS. This will happen during loss of AC Power feeding the UPS. The action taken by the drive is configured by 14:20 [UPS on Batt Actn]. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 4 ‘PERIFl Flts’ | 14:20 [UPS on Batt Actn] | —
Configurable | 159 | UPS Battery Low | UPS Battery Low This condition is raised when the level of the internal battery is Low and is indicated by the diagnostic signal from the UPS. The action taken by the drive is configured by 14:21 [UPSBatt Low Actn]. | — | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 4 ‘PERIFl Flts’ | 14:21 [UPSBatt Low Actn] | —
Fault Major | 162 | HECS +24V Loss | HECS +24V Power Loss This condition indicates that the HECS +24V power supply voltage is greater than 24.97V or lower than 20.43V. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault Major | 163 | HECS -24V Loss | HECS -24V Power Loss This condition indicates that the HECS -24V power supply voltage is lower than -24.97V or greater than -20.43V. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault Major | 164 | Ctrl +12V Loss | Control +12V Loss This condition indicates that the Control +12V power supply voltage is greater than 13.2V or less than 10.8V. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault Major | 165 | Ctrl -12V Loss | Control -12V Loss This condition indicates that the Control -12V power supply voltage is lower than -13.2V or greater than -10.8V. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault Major | 166 | Ctrl 5V Loss | Control 5V Loss This condition indicates that the Control 5V power supply voltage is greater than 5.4V or less than 4.6V. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault Major | 167 | Ctrl 3.3V Loss | Control 3.3V Loss This condition indicates that the Control 3.3V power supply voltage is greater than 3.47V or less than 3.14V. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault Major | 168 | Ctrl 2.5V Loss | Control 2.5V Loss This condition indicates that the Control 2.5V power supply voltage is greater than 2.63V or less than 2.375V. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault Major | 169 | Ctrl 1.2V Loss | Control 1.2V Loss This condition indicates that the Control 1.2V power supply voltage is greater 1.25V or less than 1.146V. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault Major | 170 | PointIO 24V Loss | Point IO 24V Loss This condition indicates that the Point IO 24V power supply voltage is greater than 24.97V or lower than 20.43V. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault Major | 171 | Ctrl 1.1V Loss | Control 1.1V Loss This condition indicates that the Control 1.1V power supply voltage is greater 1.15V or less than 1.05V | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Alarm 1 | 172 | Redn 24V Ctrl A | Redundant PwrSup 1A Fail This condition indicates that the Power Supply PS1A, used for Control Power, has failed. This is an alarm condition as the drive can continue to operate with the second power supply PS1B. | — | — | — | —
Alarm 1 | 173 | Redn 24V Ctrl B | Redundant PwrSup 1B Fail This condition indicates that the Power Supply PS1B, used for Control Power, has failed. This is an alarm condition as the drive can continue to operate with the second power supply PS1A. | — | — | — | —
Alarm 1 | 174 | Redn +24V HECS A | Redundant PwrSup 3A Fail This condition indicates that the Power Supply PS3A, used for +24V HECS Power, has failed. This is an alarm condition, as the drive can continue to operate with the second power supply PS3B. | — | — | — | —
Alarm 1 | 175 | Redn +24V HECS B | Redundant PwrSup 3B Fail This condition indicates that the Power Supply PS3B, used for +24V HECS Power, has failed. This is an alarm condition, as the drive can continue to operate with the second power supply PS#A. | — | — | — | —
Alarm 1 | 176 | Redn -24V HECS A | Redundant PwrSup 4A Fail This condition indicates that the Power Supply PS4A, used for -24V HECS Power, has failed. This is an alarm condition, as the drive can continue to operate with the second power supply PS4B. | — | — | — | —
Alarm 1 | 177 | Redn -24V HECS B | Redundant PwrSup 4B Fail This condition indicates that the Power Supply PS4B, used for -24V HECS Power, has failed. This is an alarm condition, as the drive can continue to operate with the second power supply PS4A. | — | — | — | —
Alarm 1 | 178 | Redn PwrSup 2A | Redundant PwrSup 2A Fail This condition indicates that the Power Supply 2A has failed. This is an alarm condition, as the drive can continue to operate with the second power supply 2B. | — | — | — | —
Alarm 1 | 179 | Redn PwrSup 2B | Redundant PwrSup 2B Fail This condition indicates that the Power Supply 2B has failed. This is an alarm condition, as the drive can continue to operate with the second power supply 2A. | — | — | — | —
Fault Major | 180 | Redn 24V Control | Redundant PwrSup 1 Fail This condition indicates that both Power Supplies PS1A and PS1B, used for Control Power, have failed. The drive will Coast stop. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault Major | 181 | Redn +24V HECS | Redundant PwrSup 3 Fail This condition indicates that both Power Supplies PS3A and PS3B, used for +24V HECS, have failed. The drive will Coast stop. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault Major | 182 | Redn -24V HECS | Redundant PwrSup 4 Fail This condition indicates that both Power Supplies PS4A and PS4B, used for -24V HECS, have failed. The drive will Coast stop. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault Major | 183 | IntDrvLnk CfgErr | Internal Drive Link Error This condition indicates that the firmware did not detect any Point IO modules. Check the 24V power feeding the Point IO subsystem. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault Major | 184 | Node 1 Faulted | Node 1 Faulted This condition indicates either a configuration error or a failed device on the specific node. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault Major | 185 | Node 2 Faulted | Node 2 Faulted This condition indicates either a configuration error or a failed device on the specific node. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault Major | 186 | Node 3 Faulted | Node 3 Faulted This condition indicates either a configuration error or a failed device on the specific node. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault Major | 187 | Node 4 Faulted | Node 4 Faulted This condition indicates either a configuration error or a failed device on the specific node. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault Major | 188 | Node 5 Faulted | Node 5 Faulted This condition indicates either a configuration error or a failed device on the specific node. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault Major | 189 | Node 7 Faulted | Node 6 Faulted This condition indicates either a configuration error or a failed device on the specific node. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault Major | 190 | RednPwrSup2 Fail | Redundant PwrSup 2 Fail This condition indicates that Power Supplies 2A and 2B have failed. The drive will Coast stop. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault Major | 196 | Node 1 Not Found | Node 1 Not Found This condition indicates that the specific Point IO Node is not responding on the network. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault Major | 197 | Node 2 Not Found | Node 2 Not Found This condition indicates that the specific Point IO Node is not responding on the network. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault Major | 198 | Node 3 Not Found | Node 3 Not Found This condition indicates that the specific Point IO Node is not responding on the network. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault Major | 199 | Node 4 Not Found | Node 4 Not Found This condition indicates that the specific Point IO Node is not responding on the network. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault Major | 200 | Node 5 Not Found | Node 5 Not Found This condition indicates that the specific Point IO Node is not responding on the network. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault Major | 201 | Node 7 Not Found | Node 7 Not Found This condition indicates that the specific Point IO Node is not responding on the network. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault Major | 202 | DrvLnkCfgMisMtch | Internal Drive Link Config Mismatch This condition indicates that the detected Point IO configuration does not match the DHCF. | — | Coast Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Alarm 1 | 203 | Redn24VFanXfmr1A | Xfmr1 Redn PwrSup A Fail This condition indicates that the Power Supply 5A, used for Point IO modules in the Transformer 1 cabinet, has failed. This is an alarm condition as the drive can continue to operate with the second power supply 5B. | — | — | — | —
Alarm 1 | 204 | Redn24VFanXfmr1B | Xfmr1 Redn PwrSup B Fail This condition indicates that the Power Supply 5B, used for Point IO modules in the Transformer 1 cabinet, has failed. This is an alarm condition as the drive can continue to operate with the second power supply 5A. | — | — | — | —
Alarm 1 | 205 | Redn24VFanXfmr2A | Xfmr1 Redn PwrSup A Fail This condition indicates that the Power Supply 6A, used for Point IO modules in the Transformer 2 cabinet, has failed. This is an alarm condition as the drive can continue to operate with the second power supply 6B. | — | — | — | —
Alarm 1 | 206 | Redn24VFanXfmr2B | Xfmr1 Redn PwrSup B Fail This condition indicates that the Power Supply 6B, used for Point IO modules in the Transformer 2 cabinet, has failed. This is an alarm condition, as the drive can continue to operate with the second power supply 6A. | — | — | — | —
Fault Major | 207 | 24VFanCtrl Xfmr1 | Fan 24V Point IO Xfmr 1 Fail This condition indicates that both Power Supplies 5A and 5B, used for Point IO modules in the Transformer 1 cabinet, have failed. The drive will Coast stop. | — | Coast Additional Fault Action Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Fault Major | 208 | 24VFanCtrl Xfmr2 | Fan 24V Point IO Xfmr 2 Fail This condition indicates that both Power Supplies 6A and 6B, used for Point IO modules in the Transformer 2 cabinet, have failed. The drive will Coast stop. | — | Coast Additional Fault Action Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Alarm 1 | 209 | Fan 32 Failure | Fan 32 Failure This condition indicates that the drive detected the designated fan in the Transformer Cabinet has failed, while commanding it to run. | Check the following: • Connection of the breaker and contactor to fans (All frames) • If the disconnect is closed (B-frame) • Fuses on the disconnect are not blown (B-frame / UL drive) • Health of fan motor (All frames) • Health of fan VFD (A-frame and B-frame) To check the frame type of the drive, see parameter 0:1016 [Drive Frame]. | — | — | —
Alarm 1 | 210 | Fan 33 Failure | Fan 33 Failure This condition indicates that the drive detected the designated fan in the Transformer Cabinet has failed, while commanding it to run. | Check the following: • Connection of the breaker and contactor to fans (All frames) • If the disconnect is closed (B-frame) • Fuses on the disconnect are not blown (B-frame / UL drive) • Health of fan motor (All frames) • Health of fan VFD (A-frame and B-frame) To check the frame type of the drive, see parameter 0:1016 [Drive Frame]. | — | — | —
Alarm 1 | 211 | Fan 34 Failure | Fan 34 Failure This condition indicates that the drive detected the designated fan in the Transformer Cabinet has failed, while commanding it to run. | Check the following: • Connection of the breaker and contactor to fans (All frames) • If the disconnect is closed (B-frame) • Fuses on the disconnect are not blown (B-frame / UL drive) • Health of fan motor (All frames) • Health of fan VFD (A-frame and B-frame) To check the frame type of the drive, see parameter 0:1016 [Drive Frame]. | — | — | —
Alarm 1 | 212 | Fan 35 Failure | Fan 35 Failure This condition indicates that the drive detected the designated fan in the Transformer Cabinet has failed, while commanding it to run. | Check the following: • Connection of the breaker and contactor to fans (All frames) • If the disconnect is closed (B-frame) • Fuses on the disconnect are not blown (B-frame / UL drive) • Health of fan motor (All frames) • Health of fan VFD (A-frame and B-frame) To check the frame type of the drive, see parameter 0:1016 [Drive Frame]. | — | — | —
Alarm 1 | 213 | Fan 31 Failure | Fan 31 Failure This condition indicates that the drive detected the designated fan in the Transformer Cabinet has failed, while commanding it to run. | Check the following: • Connection of the breaker and contactor to fans (All frames) • If the disconnect is closed (B-frame) • Fuses on the disconnect are not blown (B-frame / UL drive) • Health of fan motor (All frames) • Health of fan VFD (A-frame and B-frame) To check the frame type of the drive, see parameter 0:1016 [Drive Frame]. | — | — | —
Alarm 1 | 214 | Fan 36 Failure | Fan 36 Failure This condition indicates that the drive detected the designated fan in the Transformer Cabinet has failed, while commanding it to run. | Check the following: • Connection of the breaker and contactor to fans (All frames) • If the disconnect is closed (B-frame) • Fuses on the disconnect are not blown (B-frame / UL drive) • Health of fan motor (All frames) • Health of fan VFD (A-frame and B-frame) To check the frame type of the drive, see parameter 0:1016 [Drive Frame]. | — | — | —
Alarm 1 | 215 | Fan 37 Failure | Fan 37 Failure This condition indicates that the drive detected the designated fan in the Transformer Cabinet has failed, while commanding it to run. | Check the following: • Connection of the breaker and contactor to fans (All frames) • If the disconnect is closed (B-frame) • Fuses on the disconnect are not blown (B-frame / UL drive) • Health of fan motor (All frames) • Health of fan VFD (A-frame and B-frame) To check the frame type of the drive, see parameter 0:1016 [Drive Frame]. | — | — | —
Alarm 1 | 216 | Fan 38 Failure | Fan 38 Failure This condition indicates that the drive detected the designated fan in the Transformer Cabinet has failed, while commanding it to run. | Check the following: • Connection of the breaker and contactor to fans (All frames) • If the disconnect is closed (B-frame) • Fuses on the disconnect are not blown (B-frame / UL drive) • Health of fan motor (All frames) • Health of fan VFD (A-frame and B-frame) To check the frame type of the drive, see parameter 0:1016 [Drive Frame]. | — | — | —
Alarm 1 | 217 | Fan 39 Failure | Fan 39 Failure This condition indicates that the drive detected the designated fan in the Transformer Cabinet has failed, while commanding it to run. | Check the following: • Connection of the breaker and contactor to fans (All frames) • If the disconnect is closed (B-frame) • Fuses on the disconnect are not blown (B-frame / UL drive) • Health of fan motor (All frames) • Health of fan VFD (A-frame and B-frame) To check the frame type of the drive, see parameter 0:1016 [Drive Frame]. | — | — | —
Alarm 1 | 218 | Fan 40 Failure | Fan 40 Failure This condition indicates that the drive detected the designated fan in the Transformer Cabinet has failed, while commanding it to run. | Check the following: • Connection of the breaker and contactor to fans (All frames) • If the disconnect is closed (B-frame) • Fuses on the disconnect are not blown (B-frame / UL drive) • Health of fan motor (All frames) • Health of fan VFD (A-frame and B-frame) To check the frame type of the drive, see parameter 0:1016 [Drive Frame]. | — | — | —
Alarm 1 | 219 | Fan 21 Failure | Fan 21 Failure This condition indicates that the drive detected the designated fan in the the Power Cell cabinet has failed, while commanding it to run. | Check the following: • Connection of the breaker and contactor to fans (All frames) • If the disconnect is closed (B-frame) • Fuses on the disconnect are not blown (B-frame / UL drive) • Health of fan motor (All frames) • Health of fan VFD (A-frame and B-frame) To check the frame type of the drive, see parameter 0:1016 [Drive Frame]. | — | — | —
Alarm 1 | 220 | Fan 22 Failure | Fan 22 Failure This condition indicates that the drive detected the designated fan in the the Power Cell cabinet has failed, while commanding it to run. | Check the following: • Connection of the breaker and contactor to fans (All frames) • If the disconnect is closed (B-frame) • Fuses on the disconnect are not blown (B-frame / UL drive) • Health of fan motor (All frames) • Health of fan VFD (A-frame and B-frame) To check the frame type of the drive, see parameter 0:1016 [Drive Frame]. | — | — | —
Alarm 1 | 221 | Fan 23 Failure | Fan 23 Failure This condition indicates that the drive detected the designated fan in the the Power Cell cabinet has failed, while commanding it to run. | Check the following: • Connection of the breaker and contactor to fans (All frames) • If the disconnect is closed (B-frame) • Fuses on the disconnect are not blown (B-frame / UL drive) • Health of fan motor (All frames) • Health of fan VFD (A-frame and B-frame) To check the frame type of the drive, see parameter 0:1016 [Drive Frame]. | — | — | —
Alarm 1 | 222 | Fan 24 Failure | Fan 24 Failure This condition indicates that the drive detected the designated fan in the the Power Cell cabinet has failed, while commanding it to run. | Check the following: • Connection of the breaker and contactor to fans (All frames) • If the disconnect is closed (B-frame) • Fuses on the disconnect are not blown (B-frame / UL drive) • Health of fan motor (All frames) • Health of fan VFD (A-frame and B-frame) To check the frame type of the drive, see parameter 0:1016 [Drive Frame]. | — | — | —
Alarm 1 | 223 | Fan 25 Failure | Fan 25 Failure This condition indicates that the drive detected the designated fan in the the Power Cell cabinet has failed, while commanding it to run. | Check the following: • Connection of the breaker and contactor to fans (All frames) • If the disconnect is closed (B-frame) • Fuses on the disconnect are not blown (B-frame / UL drive) • Health of fan motor (All frames) • Health of fan VFD (A-frame and B-frame) To check the frame type of the drive, see parameter 0:1016 [Drive Frame]. | — | — | —
Alarm 1 | 224 | Fan 26 Failure | Fan 26 Failure This condition indicates that the drive detected the designated fan in the the Power Cell cabinet has failed, while commanding it to run. | Check the following: • Connection of the breaker and contactor to fans (All frames) • If the disconnect is closed (B-frame) • Fuses on the disconnect are not blown (B-frame / UL drive) • Health of fan motor (All frames) • Health of fan VFD (A-frame and B-frame) To check the frame type of the drive, see parameter 0:1016 [Drive Frame]. | — | — | —
Alarm 1 | 225 | Fan 27 Failure | Fan 27 Failure This condition indicates that the drive detected the designated fan in the the Power Cell cabinet has failed, while commanding it to run. | Check the following: • Connection of the breaker and contactor to fans (All frames) • If the disconnect is closed (B-frame) • Fuses on the disconnect are not blown (B-frame / UL drive) • Health of fan motor (All frames) • Health of fan VFD (A-frame and B-frame) To check the frame type of the drive, see parameter 0:1016 [Drive Frame]. | — | — | —
Alarm 1 | 226 | Fan 28 Failure | Fan 28 Failure This condition indicates that the drive detected the designated fan in the the Power Cell cabinet has failed, while commanding it to run. | Check the following: • Connection of the breaker and contactor to fans (All frames) • If the disconnect is closed (B-frame) • Fuses on the disconnect are not blown (B-frame / UL drive) • Health of fan motor (All frames) • Health of fan VFD (A-frame and B-frame) To check the frame type of the drive, see parameter 0:1016 [Drive Frame]. | — | — | —
Alarm 1 | 227 | Fan 29 Failure | Fan 29 Failure This condition indicates that the drive detected the designated fan in the the Power Cell cabinet has failed, while commanding it to run. | Check the following: • Connection of the breaker and contactor to fans (All frames) • If the disconnect is closed (B-frame) • Fuses on the disconnect are not blown (B-frame / UL drive) • Health of fan motor (All frames) • Health of fan VFD (A-frame and B-frame) To check the frame type of the drive, see parameter 0:1016 [Drive Frame]. | — | — | —
Alarm 1 | 228 | Fan 10 Failure | Fan 10 Failure This condition indicates that the drive detected the designated fan in the VFD Cabinet has failed, while commanding it to run. This is valid for Frame A drives only. | Check the following: • Connection of the breaker and contactor to fans (All frames) • If the disconnect is closed (B-frame) • Fuses on the disconnect are not blown (B-frame / UL drive) • Health of fan motor (All frames) • Health of fan VFD (A-frame and B-frame) To check the frame type of the drive, see parameter 0:1016 [Drive Frame]. | — | — | —
Alarm 1 | 229 | Fan 11 Failure | Fan 11 Failure This condition indicates that the drive detected the designated fan has failed, while commanding it to run. | Check the following: • Connection of the breaker and contactor to fans (All frames) • If the disconnect is closed (B-frame) • Fuses on the disconnect are not blown (B-frame / UL drive) • Health of fan motor (All frames) • Health of fan VFD (A-frame and B-frame) To check the frame type of the drive, see parameter 0:1016 [Drive Frame]. | — | — | —
Alarm 1 | 230 | Fan 13 Failure | Fan 13 Failure This condition indicates that the drive detected the designated fan has failed, while commanding it to run. | Check the following: • Connection of the breaker and contactor to fans (All frames) • If the disconnect is closed (B-frame) • Fuses on the disconnect are not blown (B-frame / UL drive) • Health of fan motor (All frames) • Health of fan VFD (A-frame and B-frame) To check the frame type of the drive, see parameter 0:1016 [Drive Frame]. | — | — | —
Alarm 1 | 231 | Fan 71 Failure | Fan 71 Failure This condition indicates that the drive detected the designated fan in the Filter Cabinet has failed, while commanding it to run. | Check the following: • Connection of the breaker and contactor to fans (All frames) • If the disconnect is closed (B-frame) • Fuses on the disconnect are not blown (B-frame / UL drive) • Health of fan motor (All frames) • Health of fan VFD (A-frame and B-frame) To check the frame type of the drive, see parameter 0:1016 [Drive Frame]. | — | — | —
Alarm 1 | 232 | Fan 72 Failure | Fan 72 Failure This condition indicates that the drive detected the designated fan in the Filter Cabinet has failed, while commanding it to run. | Check the following: • Connection of the breaker and contactor to fans (All frames) • If the disconnect is closed (B-frame) • Fuses on the disconnect are not blown (B-frame / UL drive) • Health of fan motor (All frames) • Health of fan VFD (A-frame and B-frame) To check the frame type of the drive, see parameter 0:1016 [Drive Frame]. | — | — | —
Major Fault | 233 | Xfrmr1FanFailure | Transformer 1 Fan Failure This condition is raised when the drive determines insufficient operational fans after a time interval specified in 14:40 [XfrmrCab Flt Dly]. 'Insufficient operational fans' will depend on whether the drive has been configured with the redundant fan option or not. If no redundancy, the loss of a single fan within a cabinet, constitutes ‘insufficient operational fans’. When redundancy is in place, two fans within the cabinet must have failed prior to declaring as ‘insufficient operational fans’. | Check for Individual Fan Failure alarm for the cabinet and follow the respective action that is specified (Fan 31...35, as applicable). | Coast Additional Fault Action Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 1 ‘LS Pwr Flts’ | — | —
Major Fault | 234 | Xfrmr2FanFailure | Transformer 2 Fan Failure This condition is raised when the drive determines insufficient operational fans after a time interval specified in 14:40 [XfrmrCab Flt Dly]. 'Insufficient operational fans' will depend on whether the drive has been configured with the redundant fan option or not. If there is no redundancy, the loss of a single fan within a cabinet, constitutes ‘insufficient operational fans’. If there is redundancy, two fans within the cabinet must have failed prior to declaring as ‘insufficient operational fans’. | Check for Individual Fan Failure alarm for the cabinet and follow the respective action that is specified (Fan 36...40, as applicable). | Coast Additional Fault Action Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 1 ‘LS Pwr Flts’ | — | —
Major Fault | 235 | FilterFanFailure | Filter Fan Failure This condition is raised when the drive determines insufficient operational fans after a time interval specified in 14:80 [FilterCab FltDly]. 'Insufficient operational fans' will depend on whether the drive has been configured with the redundant fan option or not. If there is no redundancy, the loss of a single fan within a cabinet, constitutes ‘insufficient operational fans’. If there is redundancy, two fans within the cabinet must have failed prior to declaring as ‘insufficient operational fans’. | Check for Individual Fan Failure alarm for the cabinet and follow the respective action that is specified (Fan 70 and 71, as applicable). | Coast Additional Fault Action Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Major Fault | 236 | VFDFanFailure | VFD Fan Failure This condition is raised when the drive determines insufficient operational fans after a time interval specified in 14:90 [VFDCab FltDly]. 'Insufficient operational fans' will depend on whether the drive has been configured with the redundant fan option or not. If there is no redundancy, the loss of a single fan within a cabinet, constitutes ‘insufficient operational fans’. If there is redundancy, two fans within the cabinet must have failed prior to declaring as ‘insufficient operational fans’. | Check for Individual Fan Failure alarm for the cabinet and follow the respective action that is specified (Fan 10…13, as applicable). | Coast Additional Fault Action Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 1 ‘LS Pwr Flts’ | — | —
Major Fault | 237 | Drv Cabinet Open | Drive Cabinet Door Open This condition indicates that a medium voltage cabinet door in the drive line up has been opened. | — | Coast Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: Cannot override this fault. | — | —
Major Fault | 238 | FilterThermalTrp | Filter Cabinet Thermal Trip This condition indicates the thermal sensor in the optional Filter cabinet has tripped. | — | Coast Additional Fault Action Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | — | —
Alarm 1 | 244 | Xfrmr1RTD1TmpAlm | Transformer1 RTD1 Alarm This condition is raised when 14:102 [Xfrmr1 RTD1 Fdbk] is greater than 14:101 [Xfrmr RTD FltLvl]. | — | — | — | —
Major Fault | 245 | Xfrmr1RTD1OvrTmp | Transformer1 RTD1 Overtemp This condition is raised when 14:102 [Xfrmr1 RTD1 Fdbk] is greater than 14:101 [Xfrmr RTD FltLvl]. | — | Coast Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 1 ‘LS Pwr Flts’ | — | —
Alarm 1 | 246 | Xfrmr1RTD2TmpAlm | Transformer1 RTD2 Alarm This condition is raised when 14:103 [Xfrmr1 RTD2 Fdbk] is greater than 14:101 [Xfrmr RTD FltLvl]. | — | — | — | —
Major Fault | 247 | Xfrmr1RTD2OvrTmp | Transformer1 RTD2 Overtemp This condition is raised when 14:103 [Xfrmr1 RTD2 Fdbk] is greater than 14:101 [Xfrmr RTD FltLvl]. | — | Coast Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 1 ‘LS Pwr Flts’ | — | —
Alarm 1 | 248 | Xfrmr1RTD3TmpAlm | Transformer1 RTD3 Alarm This condition is raised when 14:104 [Xfrmr1 RTD3 Fdbk] is greater than 14:101 [Xfrmr RTD FltLvl]. | — | — | — | —
Major Fault | 249 | Xfrmr1RTD3OvrTmp | Transformer1 RTD3 Overtemp This condition is raised when 14:104 [Xfrmr1 RTD3 Fdbk] is greater than 14:101 [Xfrmr RTD FltLvl]. | — | Coast Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 1 ‘LS Pwr Flts’ | — | —
Alarm 1 | 250 | Xfrmr2RTD1TmpAlm | Transformer2 RTD1 Alarm This condition is raised when 14:107 [Xfrmr2 RTD1 Fdbk] is greater than X14:101 [Xfrmr RTD FltLvl]. | — | — | — | —
Major Fault | 251 | Xfrmr2RTD1OvrTmp | Transformer2 RTD1 Overtemp This condition is raised when 14:107 [Xfrmr2 RTD1 Fdbk] is greater than X14:101 [Xfrmr RTD FltLvl]. | — | Coast Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 1 ‘LS Pwr Flts’ | — | —
Alarm 1 | 252 | Xfrmr2RTD2TmpAlm | Transformer2 RTD2 Alarm This condition is raised when 14:108 [Xfrmr2 RTD2 Fdbk] is greater than 14:101 [Xfrmr RTD FltLvl]. | — | — | — | —
Major Fault | 253 | Xfrmr2RTD2OvrTmp | Transformer2 RTD2 Overtemp This condition is raised when 14:108 [Xfrmr2 RTD2 Fdbk] is greater than 14:101 [Xfrmr RTD FltLvl]. | — | Coast Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 1 ‘LS Pwr Flts’ | — | —
Alarm 1 | 254 | Xfrmr2RTD3TmpAlm | Transformer2 RTD3 Alarm Transformer2 RTD3 Overtemp This condition is raised when 14:109 [Xfrmr2 RTD3 Fdbk] is greater than 14:101 [Xfrmr RTD FltLvl]. | — | — | — | —
Major Fault | 255 | Xfrmr2RTD3OvrTmp | Transformer2 RTD3 Overtemp This condition is raised when 14:109 [Xfrmr2 RTD3 Fdbk] is greater than 14:101 [Xfrmr RTD FltLvl]. | — | Coast Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 1 ‘LS Pwr Flts’ | — | —
Alarm 1 | 256 | Xfrmr1RTD1Ch Err | Transformer1 RTD1 Channel Error This condition indicates that the specific RTD Input in Transformer 1 is either open, shorted, or other wise returning out-of-range values. | Check for the following: • Open wires • Short-circuits • Failed sensors (measure with an Ohmmeter) • Condition of the 1734-IR2 module (measure with an Ohmmeter) For more information on troubleshooting the 1734-IR2 module, see the chapter Troubleshoot the Module, in the POINT I/O™ Thermocouple and RTD Modules User Manual, publication 1734-UM004. | — | — | —
Alarm 1 | 257 | Xfrmr1RTD2Ch Err | Transformer1 RTD2 Channel Error This condition indicates that the specific RTD Input in Transformer 1 is either open, shorted, or other wise returning out-of-range values. | Check for the following: • Open wires • Short-circuits • Failed sensors (measure with an Ohmmeter) • Condition of the 1734-IR2 module (measure with an Ohmmeter) For more information on troubleshooting the 1734-IR2 module, see the chapter Troubleshoot the Module, in the POINT I/O™ Thermocouple and RTD Modules User Manual, publication 1734-UM004. | — | — | —
Alarm 1 | 258 | Xfrmr1RTD3Ch Err | Transformer1 RTD3 Channel Error This condition indicates that the specific RTD Input in Transformer 1 is either open, shorted, or other wise returning out-of-range values. | Check for the following: • Open wires • Short-circuits • Failed sensors (measure with an Ohmmeter) • Condition of the 1734-IR2 module (measure with an Ohmmeter) For more information on troubleshooting the 1734-IR2 module, see the chapter Troubleshoot the Module, in the POINT I/O™ Thermocouple and RTD Modules User Manual, publication 1734-UM004. | — | — | —
Alarm 1 | 259 | Xfrmr2RTD1Ch Err | Transformer2 RTD1 Channel Error This condition indicates that the specific RTD Input in Transformer 2 is either open, shorted, or other wise returning out-of-range values. | Check for the following: • Open wires • Short-circuits • Failed sensors (measure with an Ohmmeter) • Condition of the 1734-IR2 module (measure with an Ohmmeter) For more information on troubleshooting the 1734-IR2 module, see the chapter Troubleshoot the Module, in the POINT I/O™ Thermocouple and RTD Modules User Manual, publication 1734-UM004. | — | — | —
Alarm 1 | 260 | Xfrmr2RTD2Ch Err | Transformer2 RTD2 Channel Error This condition indicates that the specific RTD Input in Transformer 2 is either open, shorted, or other wise returning out-of-range values. | Check for the following: • Open wires • Short-circuits • Failed sensors (measure with an Ohmmeter) • Condition of the 1734-IR2 module (measure with an Ohmmeter) For more information on troubleshooting the 1734-IR2 module, see the chapter Troubleshoot the Module, in the POINT I/O™ Thermocouple and RTD Modules User Manual, publication 1734-UM004. | — | — | —
Alarm 1 | 261 | Xfrmr2RTD3Ch Err | Transformer2 RTD3 Channel Error This condition indicates that the specific RTD Input in Transformer 2 is either open, shorted, or other wise returning out-of-range values. | Check for the following: • Open wires • Short-circuits • Failed sensors (measure with an Ohmmeter) • Condition of the 1734-IR2 module (measure with an Ohmmeter) For more information on troubleshooting the 1734-IR2 module, see the chapter Troubleshoot the Module, in the POINT I/O™ Thermocouple and RTD Modules User Manual, publication 1734-UM004. | — | — | —
Alarm 1 | 262 | Sensor1TempAlm | Sensor1 Temperature Alarm This condition is raised when 14:129 [Sensor1TempFdbk] is greater than 14:127 [Sensor1 FltLvl]. | Customer defined sensor - Check process | — | — | —
Configurable | 263 | Sensor1Overtemp | Sensor1 Temperature Fault This condition is raised when 14:129 [Sensor1TempFdbk] is greater than 14:127 [Sensor1 FltLvl]. | Customer defined sensor - Check process | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | 14:128 [Sensor1 FltActn] | —
Alarm 1 | 264 | Sensor2TempAlm | Sensor2 Temperature Alarm This condition is raised when 14:134 [Sensor2TempFdbk] is greater than 14:132 [Sensor2 FltLvl]. | Customer defined sensor - Check process | — | — | —
Configurable | 265 | Sensor2Overtemp | Sensor2 Temperature Fault This condition is raised when 14:134 [Sensor2TempFdbk] is greater than 14:132 [Sensor2 FltLvl]. | Customer defined sensor - Check process | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | 14:133 [Sensor2 FltActn] | —
Alarm 1 | 266 | Sensor3TempAlm | Sensor3 Temperature Alarm This condition is raised when 14:139 [Sensor3TempFdbk] is greater than 14:137 [Sensor3 FltLvl]. | Customer defined sensor - Check process | — | — | —
Configurable | 267 | Sensor3Overtemp | Sensor3 Temperature Fault This condition is raised when 14:139 [Sensor3TempFdbk] is greater than 14:137 [Sensor3 FltLvl]. | Customer defined sensor - Check process | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | 14:138 [Sensor3 FltActn] | —
Alarm 1 | 268 | Sensor4TempAlm | Sensor4 Temperature Alarm This condition is raised when 14:144 [Sensor4TempFdbk] is greater than 14:142 [Sensor4 FltLvl]. | Customer defined sensor - Check process | — | — | —
Configurable | 269 | Sensor4Overtemp | Sensor4 Temperature Fault This condition is raised when 14:144 [Sensor4TempFdbk] is greater than 14:142 [Sensor4 FltLvl]. | Customer defined sensor - Check process | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | 14:143 [Sensor4 FltActn] | —
Alarm 1 | 270 | Sensor5TempAlm | Sensor5 Temperature Alarm This condition is raised when 14:149 [Sensor5TempFdbk] is greater than 14:147 [Sensor5 FltLvl]. | Customer defined sensor - Check process | — | — | —
Configurable | 271 | Sensor5Overtemp | Sensor5 Temperature Fault This condition is raised when 14:149 [Sensor5TempFdbk] is greater than 14:147 [Sensor5 FltLvl]. | Customer defined sensor - Check process | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | 14:148 [Sensor5 FltActn] | —
Alarm 1 | 272 | Sensor6TempAlm | Sensor6 Temperature Alarm This condition is raised when 14:154 [Sensor6TempFdbk] is greater than 14:152 [Sensor6 FltLvl]. | Customer defined sensor - Check process | — | — | —
Configurable | 273 | Sensor6Overtemp | Sensor6 Temperature Fault This condition is raised when 14:154 [Sensor6TempFdbk] is greater than 14:152 [Sensor6 FltLvl]. | Customer defined sensor - Check process | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | 14:153 [Sensor6 FltActn] | —
Alarm 1 | 274 | Sensor7TempAlm | Sensor7 Temperature Alarm This condition is raised when 14:159 [Sensor7TempFdbk] is greater than 14:157 [Sensor7 FltLvl]. | Customer defined sensor - Check process | — | — | —
Configurable | 275 | Sensor7Overtemp | Sensor7 Temperature Fault This condition is raised when 14:159 [Sensor7TempFdbk] is greater than 14:157 [Sensor7 FltLvl]. | Customer defined sensor - Check process | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | 14:158 [Sensor7 FltActn] | —
Alarm 1 | 276 | Sensor8TempAlm | Sensor8 Temperature Alarm This condition is raised when 14:164 [Sensor8TempFdbk] is greater than 14:162 [Sensor8 FltLvl]. | Customer defined sensor - Check process | — | — | —
Configurable | 277 | Sensor8Overtemp | Sensor8 Temperature Fault This condition is raised when 14:164 [Sensor8TempFdbk] is greater than 14:162 [Sensor8 FltLvl]. | Customer defined sensor - Check process | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | 14:163 [Sensor8 FltActn] | —
Alarm 1 | 278 | Sensor9TempAlm | Sensor9 Temperature Alarm This condition is raised when 14:169 [Sensor9TempFdbk] is greater than 14:167 [Sensor9 FltLvl]. | Customer defined sensor - Check process | — | — | —
Configurable | 279 | Sensor9Overtemp | Sensor9 Temperature Fault This condition is raised when 14:169 [Sensor9TempFdbk] is greater than 14:167 [Sensor9 FltLvl]. | Customer defined sensor - Check process | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | 14:168 [Sensor9 FltActn] | —
Alarm 1 | 280 | Sensor10TempAlm | Sensor10 Temperature Alarm This condition is raised when 14:174 [Sensor10TempFdbk] is greater than 14:172 [Sensor10 FltLvl]. | Customer defined sensor - Check process | — | — | —
Configurable | 281 | Sensor10Overtemp | Sensor10 Temperature Fault This condition is raised when 14:174 [Sensor10TempFdbk] is greater than 14:172 [Sensor10 FltLvl]. | Customer defined sensor - Check process | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | 14:173 [Sensor10 FltActn] | —
Alarm 1 | 282 | Sensor11TempAlm | Sensor11 Temperature Alarm This condition is raised when 14:179 [Sensor11TempFdbk] is greater than 14:177 [Sensor11 FltLvl]. | Customer defined sensor - Check process | — | — | —
Configurable | 283 | Sensor11Overtemp | Sensor11 Temperature Fault This condition is raised when 14:179 [Sensor11TempFdbk] is greater than 14:177 [Sensor11 FltLvl]. | Customer defined sensor - Check process | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | 14:178 [Sensor11 FltActn] | —
Alarm 1 | 284 | Sensor12TempAlm | Sensor12 Temperature Alarm This condition is raised when 14:184 [Sensor12TempFdbk] is greater than 14:182 [Sensor12 FltLvl]. | Customer defined sensor - Check process | — | — | —
Configurable | 285 | Sensor12Overtemp | Sensor12 Temperature Fault This condition is raised when 14:184 [Sensor12TempFdbk] is greater than 14:182 [Sensor12 FltLvl]. | Customer defined sensor - Check process | Configurable Additional Fault Action Fault opens main circuit breaker: No Fault can automatically reset: Yes Emergency override response: 0:455 [Emerg Prot OVRD] bit 3 ‘MS Pwr Flts’ | 14:183 [Sensor12 FltActn] | —
Fault Major | 286 | Ctrl PowerLoss | Control Power Loss This condition occurs if the drive has been running for five cycles after the AC Control Power Loss event has been detected. | — | Coast Additional Fault Action Fault can automatically reset: No | — | —
Event | 287 | Ctrl PowerLoss | Control Power Loss This event indicates that the loss of AC Control power is detected. | — | — | — | —
Resettable Fault | 288 | PIOBFbrOffline 0 | PIOB Fiber Online to Offline 0 The fiber-optic communication link between the Fiber Interface Board (FIB) and the Power IO Board (PIOB) transitioned from online to offline. | Clear faults. If this fault persists, power down and then check the fiber-optic communication connections. | Coast Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 7 ‘Board Flts’ | — | —
Resettable Fault | 289 | PIOBFbrOffline 1 | PIOB Fiber Online to Offline 1 The fiber-optic communication link between the Fiber Interface Board (FIB) and the Power IO Board (PIOB) transitioned from online to offline. | Clear faults. If this fault persists, power down and then check the fiber-optic communication connections. | Coast Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 7 ‘Board Flts’ | — | —
Resettable Fault | 290 | Ctrl Msg Fiber 0 | Control Msg Watchdog Timeout 0 The watch dog timer for transmission of the Control Message between the main control board and the Power IO Board (PIOB) has timed-out. | Power down and then check the fiber-optic communication connections. If it reoccurs, replace the main control board. If it continues to reoccur, consult the factory. | Coast Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 7 ‘Board Flts’ | — | —
Resettable Fault | 291 | Ctrl Msg Fiber 1 | Control Msg Watchdog Timeout 1 The watch dog timer for transmission of the Control Message between the main control board and the Power IO Board (PIOB) has timed-out. | Power down and then check the fiber-optic communication connections. If it reoccurs, replace the main control board. If it continues to reoccur, consult the factory. | Coast Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 7 ‘Board Flts’ | — | —
Event | 292 | F32 RunTimeChngd | Fan 32 Run Time Changed This event indicates that the Fan Run Time for the specific fan was changed by the user. | — | — | — | —
Event | 293 | F33 RunTimeChngd | Fan 33 Run Time Changed This event indicates that the Fan Run Time for the specific fan was changed by the user. | — | — | — | —
Event | 294 | F34 RunTimeChngd | Fan 34 Run Time Changed This event indicates that the Fan Run Time for the specific fan was changed by the user. | — | — | — | —
Event | 295 | F35 RunTimeChngd | Fan 35 Run Time Changed This event indicates that the Fan Run Time for the specific fan was changed by the user. | — | — | — | —
Event | 296 | F31 RunTimeChngd | Fan 31 Run Time Changed This event indicates that the Fan Run Time for the specific fan was changed by the user. | — | — | — | —
Event | 297 | F36 RunTimeChngd | Fan 36 Run Time Changed This event indicates that the Fan Run Time for the specific fan was changed by the user. | — | — | — | —
Event | 298 | F37 RunTimeChngd | Fan 37 Run Time Changed This event indicates that the Fan Run Time for the specific fan was changed by the user. | — | — | — | —
Event | 299 | F38 RunTimeChngd | Fan 38 Run Time Changed This event indicates that the Fan Run Time for the specific fan was changed by the user. | — | — | — | —
Event | 300 | F39 RunTimeChngd | Fan 39 Run Time Changed This event indicates that the Fan Run Time for the specific fan was changed by the user. | — | — | — | —
Event | 301 | F40 RunTimeChngd | Fan 40 Run Time Changed This event indicates that the Fan Run Time for the specific fan was changed by the user. | — | — | — | —
Event | 302 | F21 RunTimeChngd | Fan 21 Run Time Changed This event indicates that the Fan Run Time for the specific fan was changed by the user. | — | — | — | —
Event | 303 | F22 RunTimeChngd | Fan 22 Run Time Changed This event indicates that the Fan Run Time for the specific fan was changed by the user. | — | — | — | —
Event | 304 | F23 RunTimeChngd | Fan 23 Run Time Changed This event indicates that the Fan Run Time for the specific fan was changed by the user. | — | — | — | —
Event | 305 | F24 RunTimeChngd | Fan 24 Run Time Changed This event indicates that the Fan Run Time for the specific fan was changed by the user. | — | — | — | —
Event | 306 | F25 RunTimeChngd | Fan 25 Run Time Changed This event indicates that the Fan Run Time for the specific fan was changed by the user. | — | — | — | —
Event | 307 | F26 RunTimeChngd | Fan 26 Run Time Changed This event indicates that the Fan Run Time for the specific fan was changed by the user. | — | — | — | —
Event | 308 | F27 RunTimeChngd | Fan 27 Run Time Changed This event indicates that the Fan Run Time for the specific fan was changed by the user. | — | — | — | —
Event | 309 | F28 RunTimeChngd | Fan 28 Run Time Changed This event indicates that the Fan Run Time for the specific fan was changed by the user. | — | — | — | —
Event | 310 | F29 RunTimeChngd | Fan 29 Run Time Changed This event indicates that the Fan Run Time for the specific fan was changed by the user. | — | — | — | —
Event | 311 | F71 RunTimeChngd | Fan 71 Run Time Changed This event indicates that the Fan Run Time for the specific fan was changed by the user. | — | — | — | —
Event | 312 | F72 RunTimeChngd | Fan 72 Run Time Changed This event indicates that the Fan Run Time for the specific fan was changed by the user. | — | — | — | —
Event | 313 | F10 RunTimeChngd | Fan 29 Run Time Changed This event indicates that the Fan Run Time for the specific fan was changed by the user. This event indicates that the Fan Run Time for the specific fan was changed by the user. | — | — | — | —
Event | 314 | F11 RunTimeChngd | Fan 11 Run Time Changed This event indicates that the Fan Run Time for the specific fan was changed by the user. | — | — | — | —
Event | 315 | F13 RunTimeChngd | Fan 13 Run Time Changed This event indicates that the Fan Run Time for the specific fan was changed by the user. | — | — | — | —
Event | 316 | CtrlPwr Customer | Control Power Customer This event indicates that AC power supply from the customer source is available. | — | — | — | —
Event | 317 | Ctrl Pwr Xfrmr | Control Power Transformer This event indicates that AC power supply from the auxiliary transformer winding is available. | — | — | — | —
Alarm 1 | 318 | FanPwrXfrmr1/Fil | Fan Power Loss Transformer1/Filt Cabinet This condition indicates the opening of the CB feeding 460V fan power to the Transformer 1 and optional Filter cabinet. The status is indicated by parameter 14:31 [Fan Power Status]. | — | — | — | —
Alarm 1 | 319 | FanPwr PowerCell | Loss of Fan Power for Power Cell Cabinet This condition indicates the opening of the CB feeding 460V fan power to the Power Cell cabinet. The status is indicated by parameter 14:31 [Fan Power Status]. | — | — | — | —
Alarm 1 | 320 | FanPwr Xfrmr2 | Fan Power Loss Transformer2 Cabinet This condition indicates the opening of the CB feeding 460V fan power to the Transformer 2 cabinet. The status is indicated by parameter 14:31 [Fan Power Status]. | — | — | — | —
Alarm 1 | 321 | FanPwr VFD | Loss of Fan Power for VFD Cabinet This condition indicates the opening of the CB feeding 460V fan power to the VFD cabinet. The status is indicated by parameter 14:31 [Fan Power Status]. | — | — | — | —
Event | 322 | Power Down PIOB | Power Down PIOB This conditon indicates that the Power IO Board (PIOB) received a 24V Voltage Monitor fault IRQ. | — | — | — | —
Resettable Fault | 323 | VltgSensBoardFlt | Voltage Sensing Board Fault This condition indicates that the Voltage Sensing Board is not plugged into the Power IO Board (PIOB). | Check wiring connections. | Coast (Motor Side Inverter) Additional Fault Action Fault opens main circuit breaker: Yes Fault can automatically reset: No Emergency override response: 0:455 [Emerg Prot OVRD] bit 7 ‘Board Flts’ | — | —
Alarm 1 | 324 | UsrSensor1Ch Err | User Sensor 1 Channel Error This condition indicates that the specific User Thermal Input is either open, shorted, or otherwise returning out-of-range values. | — | — | — | —
Alarm 1 | 325 | UsrSensor2Ch Err | User Sensor 2 Channel Error This condition indicates that the specific User Thermal Input is either open, shorted, or otherwise returning out-of-range values. | — | — | — | —
Alarm 1 | 326 | UsrSensor3Ch Err | User Sensor 3 Channel Error This condition indicates that the specific User Thermal Input is either open, shorted, or otherwise returning out-of-range values. | — | — | — | —
Alarm 1 | 327 | UsrSensor4Ch Err | User Sensor 4 Channel Error This condition indicates that the specific User Thermal Input is either open, shorted, or otherwise returning out-of-range values. | — | — | — | —
Alarm 1 | 328 | UsrSensor5Ch Err | User Sensor 5 Channel Error This condition indicates that the specific User Thermal Input is either open, shorted, or otherwise returning out-of-range values. | — | — | — | —
Alarm 1 | 329 | UsrSensor6Ch Err | User Sensor 6 Channel Error This condition indicates that the specific User Thermal Input is either open, shorted, or otherwise returning out-of-range values. | — | — | — | —
Alarm 1 | 330 | UsrSensor7Ch Err | User Sensor 7 Channel Error This condition indicates that the specific User Thermal Input is either open, shorted, or otherwise returning out-of-range values. | — | — | — | —
Alarm 1 | 331 | UsrSensor8Ch Err | User Sensor 8 Channel Error This condition indicates that the specific User Thermal Input is either open, shorted, or otherwise returning out-of-range values. | — | — | — | —
Alarm 1 | 332 | UsrSensor9Ch Err | User Sensor 9 Channel Error This condition indicates that the specific User Thermal Input is either open, shorted, or otherwise returning out-of-range values. | — | — | — | —
Alarm 1 | 333 | UsrSensor10ChErr | User Sensor 10 Channel Error This condition indicates that the specific User Thermal Input is either open, shorted, or otherwise returning out-of-range values. | — | — | — | —
Alarm 1 | 334 | UsrSensor11ChErr | User Sensor 11 Channel Error This condition indicates that the specific User Thermal Input is either open, shorted, or otherwise returning out-of-range values. | — | — | — | —
Alarm 1 | 335 | UsrSensor12ChErr | User Sensor 12 Channel Error This condition indicates that the specific User Thermal Input is either open, shorted, or otherwise returning out-of-range values. | — | — | — | —
Alarm 1 | 336 | Fan 12 Failure | Fan 12 Failure This condition indicates that the drive detected the designated fan has failed, while commanding it to run. | Check the following: • Connection of the breaker and contactor to fans (All frames) • If the disconnect is closed (B-frame) • Fuses on the disconnect are not blown (B-frame / UL drive) • Health of fan motor (All frames) • Health of fan VFD (A-frame and B-frame) To check the frame type of the drive, see parameter 0:1016 [Drive Frame]. | — | — | —
Event | 337 | F12 RunTimeChngd | Fan 12 Run Time Changed This event indicates that the Fan Run Time for the specific fan was changed by the user. | — | — | — | —
Alarm 1 | 338 | Rplc Fan31 - 90d | Replace Fan 31 in 90 days This condition indicates that the specified exhaust fan needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 339 | Rplc Fan32 - 90d | Replace Fan 32 in 90 days This condition indicates that the specified exhaust fan needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 340 | Rplc Fan33 - 90d | Replace Fan 33 in 90 days This condition indicates that the specified exhaust fan needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 341 | Rplc Fan34 - 90d | Replace Fan 34 in 90 days This condition indicates that the specified exhaust fan needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 342 | Rplc Fan35 - 90d | Replace Fan 35 in 90 days This condition indicates that the specified exhaust fan needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 343 | Rplc Fan36 - 90d | Replace Fan 36 in 90 days This condition indicates that the specified exhaust fan needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 344 | Rplc Fan37 - 90d | Replace Fan 37 in 90 days This condition indicates that the specified exhaust fan needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 345 | Rplc Fan38 - 90d | Replace Fan 38 in 90 days This condition indicates that the specified exhaust fan needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 346 | Rplc Fan39 - 90d | Replace Fan 39 in 90 days This condition indicates that the specified exhaust fan needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 347 | Rplc Fan40 - 90d | Replace Fan 40 in 90 days This condition indicates that the specified exhaust fan needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 348 | Rplc Fan21 - 90d | Replace Fan 21 in 90 days This condition indicates that the specified exhaust fan needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 349 | Rplc Fan22 - 90d | Replace Fan 22 in 90 days This condition indicates that the specified exhaust fan needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 350 | Rplc Fan23 - 90d | Replace Fan 23 in 90 days This condition indicates that the specified exhaust fan needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 351 | Rplc Fan24 - 90d | Replace Fan 24 in 90 days This condition indicates that the specified exhaust fan needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 352 | Rplc Fan25 - 90d | Replace Fan 25 in 90 days This condition indicates that the specified exhaust fan needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 353 | Rplc Fan26 - 90d | Replace Fan 26 in 90 days This condition indicates that the specified exhaust fan needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 354 | Rplc Fan27 - 90d | Replace Fan 27 in 90 days This condition indicates that the specified exhaust fan needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 355 | Rplc Fan28 - 90d | Replace Fan 28 in 90 days This condition indicates that the specified exhaust fan needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 356 | Rplc Fan29 - 90d | Replace Fan 29 in 90 days This condition indicates that the specified exhaust fan needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 357 | Rplc Fan10 - 90d | Replace Fan 10 in 90 days This condition indicates that the specified exhaust fan needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 358 | Rplc Fan11 - 90d | Replace Fan 11 in 90 days This condition indicates that the specified exhaust fan needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 359 | Rplc Fan12 - 90d | Replace Fan 12 in 90 days This condition indicates that the specified exhaust fan needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 360 | Rplc Fan13 - 90d | Replace Fan 13 in 90 days This condition indicates that the specified exhaust fan needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 361 | Rplc Fan71 - 90d | Replace Fan 71 in 90 days This condition indicates that the specified exhaust fan needs to be replaced within 90 days. | — | — | — | —
Alarm 1 | 362 | Rplc Fan72 - 90d | Replace Fan 72 in 90 days This condition indicates that the specified exhaust fan needs to be replaced within 90 days. | — | — | — | —
Event | 363 | ExhaustFnRplcAck | Exhaust Fan Replace Acknowledge Indicates that the user has acknowledged the Exhaust Fan Replacement alarm. | — | — | — | —
Alarm 1 | 364 | Tx1 Cab RTDChErr | Transformer 1 Cabinet RTD Channel Error This condition indicates that the Transformer 1 cabinet has lost temperature sensor measurement. This sensor is required for Predictive Maintenance function of the fans in the cabinet. | Check for the following: • Open wires • Short-circuits • Failed sensors (measure with an Ohmmeter) • Condition of the 1734-IR2 module (measure with an Ohmmeter) For more information on troubleshooting the 1734-IR2 module, see the chapter Troubleshoot the Module, in the POINT I/O™ Thermocouple and RTD Modules User Manual, publication 1734-UM004. | — | — | —
Alarm 1 | 365 | Tx2 Cab RTDChErr | Transformer 2 Cabinet RTD Channel Error This condition indicates that the Transformer 2 cabinet has lost temperature sensor measurement. This sensor is required for Predictive Maintenance function of the fans in the cabinet. | Check for the following: • Open wires • Short-circuits • Failed sensors (measure with an Ohmmeter) • Condition of the 1734-IR2 module (measure with an Ohmmeter) For more information on troubleshooting the 1734-IR2 module, see the chapter Troubleshoot the Module in the POINT I/O Thermocouple and RTD Modules User Manual, publication 1734-UM004. | — | — | —
Alarm 1 | 366 | Pc Cab RTDChErr | Power Cell Cabinet RTD Channel Error This condition indicates that the Power Cell cabinet has lost temperature sensor measurement. This sensor is required for Predictive Maintenance function of the fans in the cabinet. | Check for the following: • Open wires • Short-circuits • Failed sensors (measure with an Ohmmeter) • Condition of the 1734-IR2 module (measure with an Ohmmeter) For more information on troubleshooting the 1734-IR2 module, see the chapter Troubleshoot the Module, in the POINT I/O™ Thermocouple and RTD Modules User Manual, publication 1734-UM004. | — | — | —
Alarm 1 | 367 | Fil Cab RTDChErr | Filter Cabinet RTD Channel Error This condition indicates that the optonal Output Filter cabinet has lost temperature sensor measurement. This sensor is required for Predictive Maintenance function of the fans in the cabinet. | Check for the following: • Open wires • Short-circuits • Failed sensors (measure with an Ohmmeter) • Condition of the 1734-IR2 module (measure with an Ohmmeter) For more information on troubleshooting the 1734-IR2 module, see the chapter Troubleshoot the Module, in the POINT I/O™ Thermocouple and RTD Modules User Manual, publication 1734-UM004. | — | — | —
Alarm 1 | 368 | VFD Cab RTDChErr | VFD Cabinet RTD Channel Error This condition indicates that the VFD cabinet has lost temperature sensor measurement. This sensor is required for Predictive Maintenance function of the fans in the cabinet. | Check for the following: • Open wires • Short-circuits • Failed sensors (measure with an Ohmmeter) • Condition of the 1734-IR2 module (measure with an Ohmmeter) For more information on troubleshooting the 1734-IR2 module, see the chapter Troubleshoot the Module, in the POINT I/O™ Thermocouple and RTD Modules User Manual, publication 1734-UM004. | — | — | —

## Tables & Graphics
73 DigIn Cfg B
Digital Input combinations marked ‘•’ will cause an alarm.
| DI Stop Mode B | DI Speed Sel 2 | DI Speed Sel 1 | DI Speed Sel 0 | DI Manual Ctrl | DI Decel 2 | DI Accel 2 | DI Fwd Reverse | DI Jog 2 Reverse | DI Jog 2 Forward | DI Jog 2 | DI Jog 1 Reverse | DI Jog 1 Forward | DI Jog 1 | DI Run Reverse | DI Run Forward | DI Run | DI Start | DI HOA Start | DI Clear Fault | DI Aux Fault | DI Cur Lmt Stop | DI Coast Stop | DI Stop
DI Stop
DI Coast Stop
DI Cur Lmt Stop
DI Aux Fault
DI Clear Fault
DI HOA Start | [8 empty] | • | • |  | • | • |  | • | • | • | •
DI Start | [8 empty] | • | • |  | • | • |  | • | • | • |  | •
DI Run | [8 empty] | • | • |  | • | • |  | • | • |  | • | •
DI Run Forward | [7 empty] | • |  |  | • |  |  | • |  |  | • | • | •
DI Run Reverse | [7 empty] | • |  |  | • |  |  | • |  |  | • | • | •
DI Jog 1 | [8 empty] | • | • |  | • | • |  | • | •
DI Jog 1 Forward | [7 empty] | • |  |  | • |  |  | • |  |  | • | • | •
DI Jog 1 Reverse | [7 empty] | • |  |  | • |  |  | • |  |  | • | • | •
DI Jog 2 | [8 empty] | • | • |  | • | • |  | • | •
DI Jog 2 Forward | [7 empty] | • |  |  | • |  |  | • |  |  | • | • | •
DI Jog 2 Reverse | [7 empty] | • |  |  | • |  |  | • |  |  | • | • | •
DI Fwd Reverse | [8 empty] | • | • |  | • | • |  | • | •
DI Accel 2
DI Decel 2
DI Manual Ctrl
DI Speed Sel 0
DI Speed Sel 1
DI Speed Sel 2
DI Stop Mode B
74 DigIn Cfg C
Digital Input combinations marked ‘•’ will cause an alarm.
| DI Stop Mode B | DI Speed Sel 2 | DI Speed Sel 1 | DI Speed Sel 0 | DI Manual Ctrl | DI Decel 2 | DI Accel 2 | DI Fwd Reverse | DI Jog 2 Reverse | DI Jog 2 Forward | DI Jog 2 | DI Jog 1 Reverse | DI Jog 1 Forward | DI Jog 1 | DI Run Reverse | DI Run Forward | DI Run | DI Start | DI HOA Start | DI Clear Fault | DI Aux Fault | DI Cur Lmt Stop | DI Coast Stop | DI Stop
DI Stop |  | • | • | • | • | • | • | • | • | • |  | • | • |  | • | • | • | • | • | • | • | • | •
DI Coast Stop |  | • | • | • | • | • | • | • | • | • |  | • | • |  | • | • | • | • | • | • | • | • |  | •
DI Cur Lmt Stop |  | • | • | • | • | • | • | • | • | • |  | • | • |  | • | • | • | • | • | • | • |  | • | •
DI Aux Fault |  | • | • | • | • | • | • | • | • | • | • | • | • | • | • | • | • | • | • | • |  | • | • | •
DI Clear Fault |  | • | • | • | • | • | • | • | • | • |  | • | • |  | • | • | • |  |  |  | • | • | • | •
DI HOA Start |  | • | • | • |  | • | • | • |  |  | • |  |  | • | [6 empty] | • | • | • | •
DI Start |  | • | • | • |  | • | • | • |  |  | • |  |  | • | [6 empty] | • | • | • | •
DI Run |  | • | • | • | • | • | • | • |  |  | • |  |  | • | [5 empty] | • | • | • | • | •
DI Run Forward |  | • | • | • | • | • | • |  | • | • |  | • | • |  | • |  |  |  |  | • | • | • | • | •
DI Run Reverse |  | • | • | • | • | • | • |  | • | • |  | • | • |  |  | • |  |  |  | • | • | • | • | •
DI Jog 1 |  | • | • | • |  | • | • | • |  |  | • | [5 empty] | • | • | • |  | •
DI Jog 1 Forward |  | • | • | • | • | • | • |  | • | • |  | • |  |  | • | • |  |  |  | • | • | • | • | •
DI Jog 1 Reverse |  | • | • | • | • | • | • |  | • | • |  |  | • |  | • | • |  |  |  | • | • | • | • | •
DI Jog 2 |  | • | • | • |  | • | • | • | [5 empty] | • |  |  | • | • | • |  | •
DI Jog 2 Forward |  | • | • | • | • | • | • |  | • |  |  | • | • |  | • | • |  |  |  | • | • | • | • | •
DI Jog 2 Reverse |  | • | • | • | • | • | • |  |  | • |  | • | • |  | • | • |  |  |  | • | • | • | • | •
DI Fwd Reverse |  | • | • | • | • | • | • |  |  |  | • |  |  | • |  |  | • | • | • | • | • | • | • | •
DI Accel 2 |  | • | • | • | • |  |  | • | • | • | • | • | • | • | • | • | • | • | • | • | • | • | • | •
DI Decel 2 |  | • | • | • | • |  |  | • | • | • | • | • | • | • | • | • | • | • | • | • | • | • | • | •
DI Manual Ctrl |  | • | • | • |  | • | • | • | • | • |  | • | • |  | • | • | • |  |  | • | • | • | • | •
DI Speed Sel 0 |  | • | • |  | • | • | • | • | • | • | • | • | • | • | • | • | • | • | • | • | • | • | • | •
DI Speed Sel 1 |  | • |  | • | • | • | • | • | • | • | • | • | • | • | • | • | • | • | • | • | • | • | • | •
DI Speed Sel 2 |  |  | • | • | • | • | • | • | • | • | • | • | • | • | • | • | • | • | • | • | • | • | • | •
DI Stop Mode B