ROCKWELL AUTOMATION	PROCUREMENT SPECIFICATION

PROCUREMENT SPECIFICATION

Bulletin 280D/281D ArmorStart( Safety

Distributed Motor Control with

Full Voltage/Full Voltage Reversing Motor Starting

NOTICE: The specification guidelines in this document are intended to aid in the specification of products. Specific installations have specific requirements, and Rockwell Automation does not recommend or intend any specific application based solely upon the guidelines provided here. Because of the variety of uses for this information, the user of, and those responsible for applying this information, are responsible for ensuring the acceptability of each application and appropriate use of the guidelines. In no event will Rockwell Automation be liable for misuse, misapplication or reliance on these guidelines in connection with any specific application. Rockwell Automation also disclaims indirect or consequential damages resulting from the use or application of this information.

Note: To download or view a .doc file version of this procurement specification, please visit:
www.rockwellautomation.com/industries/procurement-specifications

TABLE OF CONTENTS

PART 1 GENERAL	3

1.01	QUALIFICATIONS	3

1.02	REFERENCES	3

1.03	ENVIRONMENTAL REQUIREMENTS	4

1.04	PRE-MANUFACTURE SUBMITTALS	4

1.05	FINAL SUBMITTALS	4

PART 2 PRODUCTS	5

2.01	DESCRIPTION	5

2.02	RATINGS	5

2.03	CONSTRUCTION	6

2.04	COMMUNICATIONS	7

2.05	CONFIGURATION	7

2.06	FUNCTIONS	7

2.07	DETAILED SPECIFICATION	8

2.08	DIMENSIONS AND WEIGHT	9

PART 3 EXECUTION	9

3.01	DELIVERY, STORAGE AND HANDLING	9

3.02	INSTALLATION	9

3.03	SPARE MATERIALS	9

3.04	WARRANTY	10

SECTION XX XX XX

SAFETY VERSION DISTRIBUTED MOTOR CONTROL WITH

FULL VOLTAGE/FULL VOLTAGE REVERSING MOTOR STARTING

- GENERAL

QUALIFICATIONS

Manufacturer

The manufacturer shall have a minimum of 25 years of experience in the manufacture of distributed motor control.

The approved manufacturers are:

Rockwell Automation Allen-Bradley

Substitutions: None permitted

Support

The manufacturer shall maintain factory trained and authorized service facilities within 100 miles of the project and shall have a demonstrated record of service for at least the previous ten years.

Support personnel are to be direct employees of the manufacturer and be available 24 hours per day through a toll-free number.

The manufacturer shall provide all required start-up and training services.

The approved manufacturers are:

Rockwell Automation Customer Support & Maintenance

Substitutions: None permitted

Certification

To ensure all quality and corrective action procedures are documented and implemented, all manufacturing locations shall be certified to the ISO-9001 Series of Quality Standards.

Third-party manufacturers and brand labeling shall not be allowed.

REFERENCES

The distributed motor control (DMC) shall be suitable for safety applications up to Safety Category 4 PLe (TÜV assessment per ISO 13849-1:2008).

The DMC shall be designed to meet or exceed the applicable requirements to comply with the standards:

UL/CSA

UL 508

CSA C22.2, No. 14

EN/IEC

EN/IEC 60947-4

EN/IEC 60947-4-1

CE Marked per Low Voltage Directive 2006/95/EC and EMC Directive 2004/108/EC

CCC

ODVA for DeviceNet

The DMC shall be certified cULus (File No. E3125, Guide NLDX, NLDX7).

ENVIRONMENTAL REQUIREMENTS

The supplier shall confirm specified service conditions during and after installation of products.

The supplier shall maintain the area free of dirt and dust during and after installation of products.

PRE-MANUFACTURE SUBMITTALS

Refer to Section _________ for submittal procedures.

Product Data

Publications on distributed motor control.

Data sheets on all furnished options.

Specification Response

Detailed response to this specification showing where in the literature each requirement is satisfied.

Clearly identified clarifications and exceptions.

Installation Instructions

A copy of the manufacturer’s installation instructions, including receiving, handling and storage instructions.

Testing and Test Reports

Testing per manufacturer’s standard.

A copy of the test reports, if available, shall be provided as part of the final documentation.

FINAL SUBMITTALS

Refer to Section ________ for procedure on submittal of final documentation.

Supplier Certification

The supplier shall provide certification that the distributed motor control has been installed in accordance with the manufacturer’s instructions.

The supplier shall provide certification that the distributed motor control settings have been properly adjusted.

Final Drawings

The manufacturer shall provide final drawings reflecting the “As-Shipped” state of the installed equipment.

Manufacturer drawings shall be provided in DWG format.

Manufacturer drawings do not need to be stamped if a drawing schedule is provided that lists the drawing numbers, revision levels, and status of drawings (Preliminary, Approval, Final, etc.).

The supplier shall be responsible for making any changes to the “As-Shipped” drawings from the manufacturer to reflect any field modifications.

Maintenance Data

Distributed motor control installation instructions and User Manual.

Parameter listing with final settings.

Field service report from start-up service.

Name and phone number for a local distributor for the spare parts.

PRODUCTS

DESCRIPTION

Allen-Bradley – Bulletin 280D/281D ArmorStart Safety Distributed Motor Control with Full Voltage/Full Voltage Reversing Motor Starting (No substitutions)

RATINGS

The distributed motor control (DMC) shall support a three-phase induction motor. DMC power circuit ratings:

Horsepower of 0.5 to 10 HP (0.37 to 7.5 kW).

Operating voltage of 380Y/220 VAC to 480Y/277 VAC.

Operating frequency of 50/60 Hz.

The DMC shall accept control power of 24 VDC (+10%, -15%) A2.

The DMC shall be equipped with a Short Circuit Protection Device (SCPD), Performance Type 1. The DMC shall have an Irms of 30 or 65 kA @ 480Y/277 VAC or 480 VAC.

The DMC shall be UL Listed for Group Motor Applications, sized per NFPA 70 (NEC) or NFPA 79.

The DMC’s environmental ratings include:

Enclosure rating of Type 4/12/13 and IP67.

Operating temperature range of -20 to +40°C (-4 to +104°F).

Relative humidity range of 5 to 95%, non-condensing.

Operating shock resistance to 15 G.

Operating vibration resistance to 1 G, 0.15 mm (0.006 in.) displacement.

Ability to operate without de-rating to an elevation of 2000 m.

Application in Pollution Degree 3 environments.

CONSTRUCTION

The distributed motor control (DMC) shall be a modular plug-n-play design in a DeviceNet safety installation and shall offer direct on-line (DOL) or direct on-line reversing (DOLR) control of a three-phase AC squirrel cage induction motor.

The DMC shall be combined with a TÜV certified safety I/O module to form a subsystem that is part of the overall machine stop function.

The DMC shall be connected to the safety I/O module through specified cable assemblies.

The DMC shall achieve Category 4 functionality by using redundant contactors.

The safety I/O module’s inputs shall monitor the status of the safety-related contactors inside the DMC.

The safety I/O module’s outputs shall provide control power to the DMC.

The DMC shall provide a local at-motor disconnect means by incorporating a motor circuit protector.

The DMC shall use quick disconnects for I/O and communications.

3-phase power, control power and motor connections shall be made via a gland plate:

Conduit/cord-ready power options with 3/4 and 1 in. conduit holes:

Trunk and drop

Daisy chain

ArmorConnect( media option. The media shall be:

produced by the DMC manufacturer, or

UL 2237 and approved for use by the DMC manufacturer.

The DMC shall be supplied with a 3-meter unshielded 4-conductor cordset.

The DMC shall include a local fault reset button and 4 status LEDs:

Power

Run

Network

Fault

The DMC shall also include externally accessible:

2 relay output connections (Micro/M12) sourced from control power (A1 and A2) with status indication.

4 inputs (Micro/M12) sourced from DeviceNet power (24 VDC) with status indication.

DeviceNet connection (Mini/M18).

Ground terminal.

A1/A2 - 24 VDC control power from the safety I/O module output.

Safety monitor input from the safety I/O module input.

The DMC shall have local control (option) with field-disable capability (except OFF):

HAND – OFF – AUTO keypad (DOL)

FORWARD – REVERSE – HAND – OFF – AUTO keypad (DOLR)

I/O points shall be used with sensors and actuators.

Two 24 VDC nominal outputs – 0.5 A per point (max 1 A total outputs).

Four 24 VDC nominal inputs – 50 mA per point (200 mA total inputs).

COMMUNICATIONS

The distributed motor control (DMC) shall allow efficient data handling on the device-level DeviceNet network.

DeviceNet addressing shall be by hard set node address switches or by software node addressing.

The DMC shall support DeviceLogix(, which allows local control using simple embedded logic.

The DMC shall provide peer-to-peer zone interlocking parameters (ZIP) to allow direct communication with up to 4 other DeviceNet nodes.

CONFIGURATION

The distributed motor control (DMC) shall have the capability to be programmed by:

Add-On Profile (AOP) for CompactLogix and ControlLogix Controllers – The AOP is used for the Logix Designer programming tool in Studio 5000( software, which is a single control platform. The AOP simplifies setup and commissioning via predefined tags and commissioning wizards and allows automatic tag generation and copy and paste functionality for quick setup and configuration of multiple DMCs. The Logix Designer programming tool is also used by the DMC’s DeviceLogix program to perform configuration locally.

RSNetWorx™ – Using the DMC’s embedded electronic data sheet (EDS), the device configuration tool RSNetWorx can configure the DMC.

FUNCTIONS

Motor control shall be of a 0.5 to 10 HP (0.37 to 7.5 kW) three-phase AC squirrel cage induction motor.

Electronic motor overload protection shall be accomplished with an I2t algorithm.

Short Circuit Protection Device (SCPD) Performance Type. The DMC shall have a rated operating current range of:

(Code B) 0.5 to 2.5 A,

(Code C) 1.1 to 5.5 A, OR

(Code D) 3.2 to 16 A

Selectable trip class of 10, 15 or 20.

Trip rating: 120% of FLC setting.

Fault diagnostics shall include:

Short Circuit

Overload

Phase Loss

Control Power Loss

Control Power Fuse Detection

I/O Fault

Output Power Fuse Detection

Over Temperature

Phase Imbalance

DeviceNet Power Loss

EEprom Fault

Hardware Fault

Device status parameters shall include:

Hdw Inputs

Network Inputs

Network Outputs

Trip Status

Starter Status

DNet Status

Starter Command

Breaker Type

Last Pr Fault

Warning Status

Phase A Current

Phase B Current

Phase C Current

Average Current

% Therm Utilized

Basic configuration parameters shall include:

FLA Setting

Overload Class

OL Reset Level

DETAILED SPECIFICATION

Power circuit:

Rated Impulsed Voltage (Uimp): 4 kV

Dielectric Withstand: UL – 2200 VAC, IEC – 2500 VAC

Reset Mode: Automatic or manual

Utilization Category: AC-3

DeviceNet:

DeviceNet Supply Voltage Rating Range: 11 to 25 VDC, 24 VDC nominal

DeviceNet Input Current:

167 mA @ 24 VDC – 4.0 W

364 mA @ 11 VDC – 4.0 W

DeviceNet Input Current Surge: 15 A for 250 (s

Baud Rates: 125, 250, 500 kbps

Distance Maximum:

500 m (1630 ft) @ 125 kbps

200 m (656 ft) @ 250 kbps

100 m (328 ft) @ 500 kbps

DIMENSIONS AND WEIGHT

The dimensions of the distributed motor control (DMC) shall not exceed 287.5 mm (11.32 in.) height x 351 mm (11.82 in.) width x 243 mm (9.57 in.) depth with motor connection cable (DOL) [or x 351 mm (13.78 in.) depth with motor connection cable (DOLR)].

The approximate weight of the DMC shall be 6.8 kg (15 lb).

EXECUTION

DELIVERY, STORAGE AND HANDLING

The supplier shall coordinate the shipping of equipment.

The supplier shall store the equipment in a clean and dry space.

The supplier shall protect the units from dirt, water, construction debris and traffic.

INSTALLATION

The supplier shall verify all distributed motor control components have been installed not exceeding the specifications or with proper derating prior to energizing.

The supplier shall follow local code and regulations with regard to electrical installation.

The supplier shall provide reasonable protection against accidental damage to component and associated cables.

The supplier shall ensure accessibility to diagnostic lights, communication ports and connection. These components shall be free from obstruction at all times.

The supplier shall verify all distributed motor control settings have been properly adjusted prior to energizing.

SPARE MATERIALS

The supplier shall provide one (1) spare distributed motor control of each size utilized, including options.

WARRANTY

The manufacturer shall provide their standard parts warranty for eighteen (18) months from the date of shipment or twelve (12) months from the date of being energized, whichever occurs first.

The manufacturer shall confirm this warranty as part of the submittal.

END OF SECTION

Rockwell Automation, Rockwell Software, Allen-Bradley, ArmorConnect, ArmorStart, DeviceLogix, RSNetWorx and Studio 5000 are trademarks of Rockwell Automation, Inc.

Trademarks not belonging to Rockwell Automation are property of their respective companies.